## Sheet1
SL.NO | DESCRIPTION | UNIT | QTY | Price Per curtain | Final Amount
1 | Supply, Installation, Testing and Commissioning of automatic fire curtains manufactured in accordance with Latest norms of BS 8524-1:2013 & BS EN 1634-1:2014+A1:2018. Rated upto 240 minutes integrity at 1000 degrees centigrade. The fire curtain assembly briefly comprised a galvanised mild steel headbox containing a steel tube curtain roller mechanism, referenced ‘Motor type 80G’, galvanised mild steel guide rails and a micronized aluminium coated stainless steel reinforced glass cloth curtain fabric and sewn with polymer coated stainless steel thread and conforms to BS476-6:1989 + A1:2009 & BS476-7:1997 (colour –Grey) . System classified to 13501-1:2007+ A1 2009. The motor is a patented 24v DC gravity fail safe tubular motor and is controlled through a panel which includes a battery back-up and a warning siren. The control panel requires a 230/240V UPS AC supply @ 50Hz . In the event of a complete power failure, the curtain will descend under gravity but will retract when power is restored. An emergency retract switch will be sited each side of the curtain to override the programme. The fire curtain system is delivered complete and ready to install, with the head box containing the barrel, motor, curtain and bearings assembled and sealed. Other parts to be assembled on site. All controls are set from the panel provided
All parts will be presented in a powder coated finish to the client’s specification.
A certificate of compliance will be issued following commissioning. authorization letter from the manufacturer or principal that he is representing. The Fire curtain must be compliant to BS 8524-1, BS EN 1634-1.
This shall be integrated with the electrical, BMS, FIre/ Smoke detection system, etc, to ensure complete functionality. The entire system to be designed and executed as per the EN code provisions and tolerances. Contractor to produce design & shop drawings for approval as per Project Consultant / Engineer-in-charge. The work shall be guaranteed for all material & constructional defects. The rate shall include for Design, fabrication, submission & approval of design & shop drawings prior to supply & installation of the Fire Curtains as per design intent drawings. The clear openable size for the Fire curtain as per drawings. Respective Technical Test Certifications and other documents must be submitted to Consultant for approval.
1.1 | Note : Below dimensions are indicative only, vendor need to evalveted actual dimension's as per site / final architecture plan and +/- 10% additional qty. on each line item is to be considered.
For easy fire evacuation overlap / sutiable system to be offer in exit route - Refer Drawings.
1.1 | Automatice Fire Curtains size to be 2200mm (W) X 3500mm (H) Single Barrel with Egrees Door. | Set | 8.00 | 154880 | 1239040
1.2 | Automatice Fire Curtains size to be 2750mm (W) X 3500mm (H) Single Barrel with Egrees Door. | Set | 2.00 | 179168 | 358336
1.3 | Automatice Fire Curtains size to be 3100mm (W) X 3500mm (H) Single Barrel with Egrees Door. | Set | 1.00 | 203280 | 203280
1.4 | Automatice Fire Curtains size to be 2950mm (W) X 3500mm (H) Single Barrel with Egrees Door. | Set | 1.00 | 203280 | 203280
SUB TOTAL |  |  |  |  | 2003936
GST 18% |  |  |  |  | 360708.48
FINAL AMOUNT |  |  |  |  | 2364644.48
Terms & Conditions:
1.Payment Term: 50 % Advance againest PO and 50% before material dispatching
2. Delivery within 4-5weeks from date of release of purchase order approved drawing and advance payment.
3.Scaffolding support to hang the curtain will be provided by the client
4.However any civil work/civil modification location to install the curtain to be done by client
5.Installation is also included in the above price
6.Power supply for installation to be provided by client
7. All goods will remain the property of WindowTechs until paid for in full. We reserve the right to remove any units fitted by ourselves or others until full payment is received.
8.This quote is valid for 60 days only
9. As per Section 16 of the MSME Act, the buyer is liable to pay interest with the monthly rests to the supplier in case of non-payment or delayed payment. The interest is compounded at the rate of 24%.
Regards,
For Window Techs India Pvt.Ltd
Alistair Paiva