## BOQ -Fire curtain
DETAILED ESTIMATE - FIRE CURTAIN
SL. | DWG NO | CODE NO | ITEM DESCRIPTION | LOCATION | BASIC RATE | UNIT | FLOORWISE QTY | [30 empty] | COSTING | [16 empty] | REMARKS | MAKE QUOTED BY THE VENDORS | STPI BENEFIT (YES/NO)
[7 empty] | B1 | [6 empty] | B2 | [6 empty] | B3 | [5 empty] | AMENITIES | [5 empty] | TOTAL - QTY |  |  |  |  | RATE |  | B1 |  |  | B2 |  |  | B3 |  |  | AMENITIES |  |  | GRAND TOTAL
[7 empty] | LOWER G FLR | G FLR | 1ST FLR | 2ND FLR | 3RD FLR | 4TH FLR | TOTAL | UPPER BASEMENT | G FLR | 1ST FLR | 2ND FLR | AUDITORIUM ENTRANCE | AUDITORIUM MEZZANINE | TOTAL | LOWER BASEMENT | UPPER BASEMENT | G FLR | 1ST FLR | 2ND FLR | TOTAL | CRECHE (GF) | CRECHE (1ST FLR) | KITCHEN BLOCK | TRANSIT HUB | ENTRY PAVILION | TOTAL | B1 | B2 | B3 | AMENITIES | GRAND TOTAL | SUPPLY RATE (INR) | INST.RATE (INR) | SUPPLY AMOUNT (INR) | INST. AMOUNT (INR) | TOTAL AMOUNT (INR) | SUPPLY AMOUNT (INR) | INST. AMOUNT (INR) | TOTAL AMOUNT (INR) | SUPPLY AMOUNT (INR) | INST. AMOUNT (INR) | TOTAL AMOUNT (INR) | SUPPLY AMOUNT (INR) | INST. AMOUNT (INR) | TOTAL AMOUNT (INR) | SUPPLY AMOUNT (INR) | INST. AMOUNT (INR) | TOTAL AMOUNT (INR)
[13 empty] | 0 | [6 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  |  | FIRE CURTAINS | [29 empty] | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | FIRE AND SMOKE CURTAIN SYSTEM - 2 HRS INTEGRITY @ 1000 Deg C | [29 empty] | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SITC "Fire Curtains" with galvanized MS head box, size( 200X200/400mm) powder coated, side guides size( 53x100mm) along with adjustment channels & bottom bars with motors for power up operation with gravity fail safe with standard battery backup minimm 2 hours & operated system fixed into steel rollers with woven glass fibre fabric, reinforced with stainless steel wire having micronized aluminium polymer coating on each side of the fabric (silver/grey) Complete OFC system shall be tested in accordance with EN 1634-1, EN 1363-1, EN 1363-2, Radiation min 90 minutes <20kW/m2 for single barrel and radiation min 120 minutes <20kW/m2 for Multiple barrel. The stitching of threads must be shown in Test report n same to be followed, the fabric material is checked independently to reaction to fire test in accordance with BS EN ISO 1716 to achieve an “A1” classification in accordance with BS EN 13501-1+A1. Vendor/Manufacturer to submit valid Test Report for the complete systems and not just for fabric from an independent international accredited laboratory. The Test Report of complete system should not be more than 5 years old. | [29 empty] | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Fire Curtains System Include: Top box, Side Guides, Bottom bar, Fabric, Barrel, PCB, 12 Volt Battery, Pull back Switch, Key Switch and GFS motor. | [29 empty] | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | The automatic smoke or fire curtain control panel requires an Uninterruptible Power Supply (UPS) of 200 V - 200 V AC with 3 core x 1.5mm thick wire in order to keep the batteries charged up. The only function of the mains supply is to keep the batteries charged up. The power required for driving the system is taken from the included batteries. The control panel should have an Uninterruptible mains power supply under normal conditions, to ensure the proper functioning of the system. These battery shall be compatable to provide the signal for BMS monitoring. | [29 empty] | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4m*5.3m |  |  | Nos |  | 2 |  |  |  |  | 2 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 2 | 0 | 0 | 0 | 2 | 276712.5 | 10000 | 553425 | 20000 | 573425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553425 | 20000 | 573425
|  |  | 8.3m*3m Specialized L Shape |  |  | Nos |  | 1 |  |  |  |  | 1 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 1 | 0 | 0 | 0 | 1 | 472702.5 | 20000 | 472702.5 | 20000 | 492702.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 472702.5 | 20000 | 492702.5
|  |  | 4.7m*2.9m |  |  | Nos |  |  | 1 | 1 | 1 | 1 | 4 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 4 | 0 | 0 | 0 | 4 | 162150 | 10000 | 648600 | 40000 | 688600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 648600 | 40000 | 688600
|  |  | 2.1m*2.9m |  |  | Nos |  |  | 2 | 1 | 1 | 1 | 5 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 5 | 0 | 0 | 0 | 5 | 103400 | 10000 | 517000 | 50000 | 567000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 517000 | 50000 | 567000
|  |  | 7.2m*3.1m |  |  | Nos |  |  |  |  | 1 |  | 1 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 1 | 0 | 0 | 0 | 1 | 300800 | 20000 | 300800 | 20000 | 320800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300800 | 20000 | 320800
|  |  | 8.7m*3.1m |  |  | Nos |  |  | 1 |  |  |  | 1 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 1 | 0 | 0 | 0 | 1 | 458250 | 20000 | 458250 | 20000 | 478250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 458250 | 20000 | 478250
|  |  | 8.3m*3.1m |  |  | Nos |  |  |  | 1 |  |  | 1 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 1 | 0 | 0 | 0 | 1 | 383050 | 20000 | 383050 | 20000 | 403050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383050 | 20000 | 403050
[6 empty] | Nos | [6 empty] | 0 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4.3m*5.3m |  |  | Nos | [6 empty] | 0 |  | 1 |  |  | 0 | 0 | 1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 1 | 0 | 0 | 1 | 276712.5 | 10000 | 0 | 0 | 0 | 276712.5 | 10000 | 286712.5 | 0 | 0 | 0 | 0 | 0 | 0 | 276712.5 | 10000 | 286712.5
|  |  | 7.6m*5.3m |  |  | Nos | [6 empty] | 0 |  | 1 |  |  | 0 | 0 | 1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 1 | 0 | 0 | 1 | 341925 | 20000 | 0 | 0 | 0 | 341925 | 20000 | 361925 | 0 | 0 | 0 | 0 | 0 | 0 | 341925 | 20000 | 361925
|  |  | 9.9m*5.3m |  |  | Nos | [6 empty] | 0 |  | 2 |  |  | 0 | 0 | 2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 2 | 0 | 0 | 2 | 682675 | 20000 | 0 | 0 | 0 | 1365350 | 40000 | 1405350 | 0 | 0 | 0 | 0 | 0 | 0 | 1365350 | 40000 | 1405350
|  |  | 5.4m*5.3m |  |  | Nos | [6 empty] | 0 |  | 3 |  |  | 0 | 0 | 3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 3 | 0 | 0 | 3 | 341337.5 | 10000 | 0 | 0 | 0 | 1024012.5 | 30000 | 1054012.5 | 0 | 0 | 0 | 0 | 0 | 0 | 1024012.5 | 30000 | 1054012.5
|  |  | 4.1m*2.9m |  |  | Nos | [6 empty] | 0 |  |  |  | 1 | 0 | 0 | 1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 1 | 0 | 0 | 1 | 144525 | 10000 | 0 | 0 | 0 | 144525 | 10000 | 154525 | 0 | 0 | 0 | 0 | 0 | 0 | 144525 | 10000 | 154525
|  |  | 11.7m*3.1m |  |  | Nos | [6 empty] | 0 |  |  | 1 |  | 0 | 0 | 1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 1 | 0 | 0 | 1 | 512887.5 | 30000 | 0 | 0 | 0 | 512887.5 | 30000 | 542887.5 | 0 | 0 | 0 | 0 | 0 | 0 | 512887.5 | 30000 | 542887.5
|  |  | 1.8m*5.3m |  |  | Nos | [6 empty] | 0 |  | 1 |  |  | 0 | 0 | 1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 1 | 0 | 0 | 1 | 115150 | 10000 | 0 | 0 | 0 | 115150 | 10000 | 125150 | 0 | 0 | 0 | 0 | 0 | 0 | 115150 | 10000 | 125150
[6 empty] | Nos | [6 empty] | 0 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 8.95m*5.3m |  |  | Nos | [6 empty] | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 0 | 1 | 1 | 2 | [5 empty] | 0 | 0 | 0 | 2 | 0 | 2 | 618050 | 20000 | 0 | 0 | 0 | 0 | 0 | 0 | 1236100 | 40000 | 1276100 | 0 | 0 | 0 | 1236100 | 40000 | 1276100
|  |  | 7.05m*5.3m |  |  | Nos | [6 empty] | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 1 |  |  | 1 | [5 empty] | 0 | 0 | 0 | 1 | 0 | 1 | 488800 | 20000 | 0 | 0 | 0 | 0 | 0 | 0 | 488800 | 20000 | 508800 | 0 | 0 | 0 | 488800 | 20000 | 508800
|  |  | 4m*5.3m |  |  | Nos | [6 empty] | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 2 |  |  | 2 | [5 empty] | 0 | 0 | 0 | 2 | 0 | 2 | 276712.5 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 553425 | 20000 | 573425 | 0 | 0 | 0 | 553425 | 20000 | 573425
|  |  | 3.6m*2.9m |  |  | Nos | [6 empty] | 0 |  |  |  |  | 0 | 0 | 0 |  |  |  | 1 | 1 | 2 | [5 empty] | 0 | 0 | 0 | 2 | 0 | 2 | 126900 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 253800 | 20000 | 273800 | 0 | 0 | 0 | 253800 | 20000 | 273800
|  |  | 2.3m*2.9m |  |  | Nos | [6 empty] | 0 |  |  |  |  | 0 | 0 | 0 |  |  |  | 1 |  | 1 | [5 empty] | 0 | 0 | 0 | 1 | 0 | 1 | 103400 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 103400 | 10000 | 113400 | 0 | 0 | 0 | 103400 | 10000 | 113400
[13 empty] | 0 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 |  |  | CONTROL PANEL | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Suitable motor for the rated operation with split drop delay. Motor capable to deliver liner velocity for curtain of min 152 mm/sec and max 610mm/sec with 2hrs fire rating for motor material. Curtains shall be in retracted mode during normal operation. Control panel shall be integreated with fire alarm panel and must have Gravity Fail Safe with battery backup of minimum 2 hours.The panel shall be powder coated. The operation shall be suitable for dedicated 240 Volts UPS, 50 Hz AC supply and should have a Key Switch for manual testing. Notificate sound required during drop of fire curtains. Optional BMS compatibility availabe. Note: The doorset was subjected to 25 manually operated opening and closing cycles as specified in EN 14600: 2005. |  |  | Nos |  | 3 | 4 | 3 | 3 | 2 | 15 |  | 8 | 1 | 1 | 0 | 0 | 10 |  |  | 3 | 3 | 2 | 8 | [5 empty] | 0 | 15 | 10 | 8 | 0 | 33 | 40000 |  | 600000 | 0 | 600000 | 400000 | 0 | 400000 | 320000 | 0 | 320000 | 0 | 0 | 0 | 1320000 | 0 | 1320000
[13 empty] | 0 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 |  |  | MANUAL INTERMITTANT PUSH BUTTON . | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MANUAL INTERMITTANT PUSH BUTTON INDUSTRIAL GRADE WITH IP 65 PROTECTION - This switch shall enusure only 1 bay Curtain shall be abort WHEN pressed and close upon release. |  |  | Nos |  | 6 | 8 | 6 | 6 | 4 | 30 |  | 16 | 2 | 2 | 0 | 0 | 20 |  |  | 6 | 6 | 4 | 16 | [5 empty] | 0 | 30 | 20 | 16 | 0 | 66 | 1000 |  | 30000 | 0 | 30000 | 20000 | 0 | 20000 | 16000 | 0 | 16000 | 0 | 0 | 0 | 66000 | 0 | 66000
[13 empty] | 0 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 |  |  | FIRE AND SMOKE CURTAIN SYSTEM - 1 HRS INTEGRITY @ 1000 Deg C | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SITC "Fire Curtains" with galvanized MS head box, size( 200X200/400mm) powder coated, side guides size( 53x100mm) along with adjustment channels & bottom bars with motors for power up operation with gravity fail safe with standard battery backup minimm 1 hours & operated system fixed into steel rollers with woven glass fibre fabric, reinforced with stainless steel wire having micronized aluminium polymer coating on each side of the fabric (silver/grey) Complete OFC system shall be tested in accordance with EN 1634-1, EN 1363-1, EN 1363-2, Radiation min 90 minutes <20kW/m2 for single barrel and radiation min 60 minutes <20kW/m2 for Multiple barrel. The stitching of threads must be shown in Test report n same to be followed, the fabric material is checked independently to reaction to fire test in accordance with BS EN ISO 1716 to achieve an “A1” classification in accordance with BS EN 13501-1+A1. Vendor/Manufacturer to submit valid Test Report for the complete systems and not just for fabric from an independent international accredited laboratory. The Test Report of complete system should not be more than 5 years old. | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Fire Curtains System Include: Top box, Side Guides, Bottom bar, Fabric, Barrel, PCB, 12 Volt Battery, Pull back Switch, Key Switch and GFS motor. | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | The automatic smoke or fire curtain control panel requires an Uninterruptible Power Supply (UPS) of 200 V - 200 V AC with 3 core x 1.5mm thick wire in order to keep the batteries charged up. The only function of the mains supply is to keep the batteries charged up. The power required for driving the system is taken from the included batteries. The control panel should have an Uninterruptible mains power supply under normal conditions, to ensure the proper functioning of the system. These battery shall be compatable to provide the signal for BMS monitoring. | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 3.3m*1.75m |  |  | Nos |  | 1 |  |  |  |  | 1 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 1 | 0 | 0 | 0 | 1 | 103400 | 10000 | 103400 | 10000 | 113400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103400 | 10000 | 113400
|  |  | 4.2m*1.75m |  |  | Nos |  | 1 |  |  |  |  | 1 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 1 | 0 | 0 | 0 | 1 | 118087.5 | 10000 | 118087.5 | 10000 | 128087.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118087.5 | 10000 | 128087.5
|  |  | 5.6m*1.75m |  |  | Nos |  | 1 |  |  |  |  | 1 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 1 | 0 | 0 | 0 | 1 | 162150 | 10000 | 162150 | 10000 | 172150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162150 | 10000 | 172150
|  |  | 12.5m*1.85m |  |  | Nos |  | 1 |  |  |  |  | 1 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 1 | 0 | 0 | 0 | 1 | 354262.5 | 30000 | 354262.5 | 30000 | 384262.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354262.5 | 30000 | 384262.5
|  |  | 7.5m*1.95m |  |  | Nos |  | 1 |  |  |  |  | 1 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 1 | 0 | 0 | 0 | 1 | 206800 | 20000 | 206800 | 20000 | 226800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206800 | 20000 | 226800
|  |  | 10.9m*1.95m |  |  | Nos | 1 | [5 empty] | 1 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 1 | 0 | 0 | 0 | 1 | 324300 | 20000 | 324300 | 20000 | 344300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324300 | 20000 | 344300
|  |  | 2.61m*4.25m |  |  | Nos | 2 | [5 empty] | 2 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 2 | 0 | 0 | 0 | 2 | 144525 | 10000 | 289050 | 20000 | 309050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 289050 | 20000 | 309050
[13 empty] | 0 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 9.9m*1.95m |  |  | Nos | [6 empty] | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 1 |  |  | 1 | [5 empty] | 0 | 0 | 0 | 1 | 0 | 1 | 294925 | 20000 | 0 | 0 | 0 | 0 | 0 | 0 | 294925 | 20000 | 314925 | 0 | 0 | 0 | 294925 | 20000 | 314925
|  |  | 10.9m*1.95m |  |  | Nos | [6 empty] | 0 |  |  |  |  | 0 | 0 | 0 |  |  | 1 |  |  | 1 | [5 empty] | 0 | 0 | 0 | 1 | 0 | 1 | 324300 | 20000 | 0 | 0 | 0 | 0 | 0 | 0 | 324300 | 20000 | 344300 | 0 | 0 | 0 | 324300 | 20000 | 344300
[13 empty] | 0 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 |  |  | CONTROL PANEL | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Suitable motor for the rated operation with split drop delay. Motor capable to deliver liner velocity for curtain of min 152 mm/sec and max 610mm/sec with 2hrs fire rating for motor material. Curtains shall be in retracted mode during normal operation. Control panel shall be integreated with fire alarm panel and must have Gravity Fail Safe with battery backup of minimum 2 hours.The panel shall be powder coated. The operation shall be suitable for dedicated 240 Volts UPS, 50 Hz AC supply and should have a Key Switch for manual testing. Notificate sound required during drop of fire curtains. Optional BMS compatibility availabe. Note: The doorset was subjected to 25 manually operated opening and closing cycles as specified in EN 14600: 2005. |  |  | Nos | 3 | 5 |  |  |  |  | 8 |  |  |  |  | 0 | 0 | 0 |  |  | 2 |  |  | 2 | [5 empty] | 0 | 8 | 0 | 2 | 0 | 10 | 40000 |  | 320000 | 0 | 320000 | 0 | 0 | 0 | 80000 | 0 | 80000 | 0 | 0 | 0 | 400000 | 0 | 400000
[13 empty] | 0 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 |  |  | MANUAL INTERMITTANT PUSH BUTTON . | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MANUAL INTERMITTANT PUSH BUTTON INDUSTRIAL GRADE WITH IP 65 PROTECTION - This switch shall enusure only 1 bay Curtain shall be abort WHEN pressed and close upon release. |  |  | Nos | 6 | 10 |  |  |  |  | 16 |  |  |  |  | 0 | 0 | 0 |  |  | 4 |  |  | 4 | [5 empty] | 0 | 16 | 0 | 4 | 0 | 20 | 1000 |  | 16000 | 0 | 16000 | 0 | 0 | 0 | 4000 | 0 | 4000 | 0 | 0 | 0 | 20000 | 0 | 20000
[13 empty] | 0 |  |  |  |  | 0 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | TOTAL AMOUNT FOR FIRE CURTAIN | [9 empty] | 0 | [6 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 |  |  | 5857877.5 | 310000 | 6167877.5 | 4200562.5 | 150000 | 4350562.5 | 3674750 | 150000 | 3824750 | 0 | 0 | 0 | 13733190 | 610000 | 14343190