## Summary
PROJECT : EY CORAL
LOCATION : BANGALORE
SUBHEAD : MEP SERVICES MODIFICATION WORKS -8TH FLOOR
MEP WORKS SUMMARY
1 | ELECTRICAL SYSTEM | 0
2 | FIRE FIGHTING WORKS | 688500
3 | HVAC WORKS | 0
4 | BMS WORKS | 0
| TOTAL | 688500
4.08
4.09
5.03

## Electrical
SUMMARY |  |  |  |  | Supply & Installation
A. | POINT WIRING | [5 empty] | 0 | 0
B | CABLES, MAINS & SUB MAINS & DISTRIBUTION BOARDS. | [5 empty] | 0 | 0
C | FIRE DETECTION SYSTEM (ANALOGUE ADDRESSABLE) | [5 empty] | 0 | 0
D | P.A. SYSTEM | [5 empty] | 0 | 0
E | SUPPLY & FIXING OF LIGHTING FIXTURES | [5 empty] | 0 | 0
| TOTAL | [5 empty] | 0 | 0
| GRAND TOTAL FOR SUPPLY AND INSTALLATION | [6 empty] | 0
Exclusion
CCTV & Access Control system.
Sl.No. | DESCRIPTION | UNIT | 8th | QTY. | Supply Rate | Installation Rate | Supply Amount | Installation Amount
[7 empty] | 0 | 0
[7 empty] | 0 | 0
A. | POINT WIRING | [5 empty] | 0 | 0
[7 empty] | 0 | 0
| Point wiring rates are exclusive of 3 x 2.5 sq mm FRLS PVC insulated stranded copper conductor wires for circuit from DB to First Switch Board | [5 empty] | 0 | 0
[7 empty] | 0 | 0
1 | Wiring for the following light points with 1.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in concealed M.S. conduits in F.ceiling/walls/ceiling as direc­ted including providing 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing comple­te as required. | [5 empty] | 0 | 0
[7 empty] | 0 | 0
a. | First point controlled by one no. 6 amp switch. | Nos. | 5 | 5 |  |  | 0 | 0
[7 empty] | 0 | 0
2 | Wiring for the following light points with 1.5 Sq.mm FRLS PVC insulated stranded copper conductor wires in Partially Existing and Partially New concealed M.S. conduits in F.ceiling/walls/ceiling as direc­ted including providing 6 amps flush type switches, 5 sided G.I Boxes for housing switc­hes and earth­ing comple­te as required. | [5 empty] | 0 | 0
[7 empty] | 0 | 0
a. | First point controlled by one no. 6 amp switch. | Nos. | 8 | 8 |  |  | 0 | 0
[7 empty] | 0 | 0
3 | Same as item No. 1 above but LOOP POINT i.e. wiring of point looped from first point with 3 x 1.5 sq. mm FRLS PVC insulated copper conductor wire in concealed/exposed MS conduit and earthing | Nos. | 15 | 15 |  |  | 0 | 0
[7 empty] | 0 | 0
4 | Same as item No. 2 above but LOOP POINT i.e. wiring of point looped from first point with 3 x 1.5 sq. mm FRLS PVC insulated copper conductor wire in Partially Existing and Partially New concealed/exposed MS conduit and earthing | Nos. | 28 | 28 |  |  | 0 | 0
[7 empty] | 0 | 0
5 | Shifting/Extension/Addition of light point including providing additional wiring from existing position to new position and new switch control as revised layout with 3 x 1.5 sq mm PVC insulated stranded copper conductor wires in M.S./Flexible Conduit, changing control of light point MCB to Switch | Nos. | 25 | 25 |  |  | 0 | 0
[7 empty] | 0 | 0
6 | Wiring for 6/16 amps light plug outlets with 3x2.5 sq.mm FRLS PVC insulated stranded copper conductor wires in M.S. Conduits in ceiling/walls/floor as direc­ted incl­u­ding providing 16 amps flush type 5 pin socket and 6 amps switch with cover plate, 5 sided G.I boxes for housing switches, sockets and earthi­ng complete as required. (for general areas) | Nos. | 10 | 10 |  |  | 0 | 0
[7 empty] | 0 | 0
7 | Wiring for Fire dampher points with 3 x 2.5 sq.mm FRLS PVC insulated stranded copper con­ductor wires in concealed M.S. conduits in F.ceiling/ walls/ Ceiling as directed including providing and fixing of 16 amps flush type switches 16 amps 3 pin socket near VRV points, 5 sided G.I. boxes for housing switches and 16 amps 3 pin socket outlet and earthing and complete as required.(including body earth for GI boxes) ( 2 to 3 points per circuits) | Nos. | 2 | 2 |  |  | 0 | 0
[7 empty] | 0 | 0
8 | Providing and fixing of 1 No.6amp flush type 3 pin international socket and 1 No. 6 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS/Raw ). GI Box to have earth pin for body earthing The circuit wiring shall be tapped from existing 3 nos UPS socket , the cost includes of removing and refixin of existing switch/ socket | Nos. | 12 | 12 |  |  | 0 | 0
[7 empty] | 0 | 0
9 | Providing and fixing of 2 Nos.6 amp flush type 3 pin international socket and 1 No. 16 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS). GI Box to have earth pin for body earthing | Nos. | 8 | 8 |  |  | 0 | 0
[7 empty] | 0 | 0
10 | Providing and fixing of 3 Nos.6 amp flush type 3 pin international socket and 1 No. 16 amps switch cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required (for UPS). GI Box to have earth pin for body earthing | Nos. | 18 | 18 |  |  | 0 | 0
[7 empty] | 0 | 0
11 | Removing, disconneting and refixing of 2/3 nos 6 amps flush type 5 pin sockets and 1no.16 amp switch with cover plate, 5 sided G.I. Boxes complete with all fixing accessories after health checkup etc. | Nos. | 12 | 12 |  |  | 0 | 0
[7 empty] | 0 | 0
12 | Removing, disconneting and refixing of 1nos 6 amps flush type 5 pin sockets and 1no.16 amp switch with cover plate, 5 sided G.I. Boxes complete with all fixing accessories after health checkup etc. | Nos. | 11 | 11 |  |  | 0 | 0
[7 empty] | 0 | 0
13 | Providing and fixing of 1 No.16 amps flush type 6 pin socket and 1 No. 16 amps switch with indicator, cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required GI Boxes to have earth pin for body earthing | Nos. | 6 | 6 |  |  | 0 | 0
[7 empty] | 0 | 0
13 | Providing and fixing of 1 No.6 amps flush type 6 pin socket and 1 No. 6 amps switch with indicator, cover plate, 5 sided G.I. Boxes for housing switches and sockets and earthing complete as required GI Boxes to have earth pin for body earthing | Nos. | 4 | 4 |  |  | 0 | 0
[7 empty] | 0 | 0
14 | Wiring for UPS plug outlets points with three core, 2.5 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694/1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor including all cable termination accessories) (including body earth for GI boxes) | RM | 450 | 450 |  |  | 0 | 0
[7 empty] | 0 | 0
15 | Wiring for UPS plug outlets points with three core, 4.0 sqmm FRLS PVC Insulated and PVC sheathed flexible cable with bright annealed electrolytic copper conductor , 1100 volt grade confirming to IS : 694/1990 with latest amendments, in existing Channels/ conduit in ceiling/walls/floor inclu­ding all cable termination accessories) Earthing of GI Box to be included | RM | 25 | 25 |  |  | 0 | 0
[7 empty] | 0 | 0
16 | Providing and fixing in position the following M.S. conduits including all accessories concealed in F. ceiling/wall/floor as required including 1.6 mm thick M.S. junction or pull boxes with 3mm thick perspex sheet cover plate compl­te with 1.6 mm dia. G.I. pull wires in the length of conduit. | [5 empty] | 0 | 0
[7 empty] | 0 | 0
a. | 20 mm dia conduit ( 1.6 mm thick) | RM | 20 | 20 |  |  | 0 | 0
b. | 25 mm dia conduit (1.6 mm thick) | RM | 110 | 110 |  |  | 0 | 0
c. | 32 mm dia conduit (2.0 mm thick) | RM | 40 | 40 |  |  | 0 | 0
[7 empty] | 0 | 0
17 | Providing and fixing in position the following G.I. flexible conduits including all accessories | [5 empty] | 0 | 0
[7 empty] | 0 | 0
a. | 1.6mmwall thickness 20mm dia | RM | 20 | 20 |  |  | 0 | 0
[7 empty] | 0 | 0
19 | Fabricating supplying to site of installation, installation on ceiling/ surface 1.6 mm thick M.S. powder coated raceways of height 50 mm and 1.2 mm thick openable cover, totally enclosed, the joints between two lengths of channels or between channel and junction box shall be joined together with 3 mm thick M.S. Powder coated coupler plates to make it dust and water proof. The cost shall including all supporting and fixing accessories including dash fasteners.(Blue colour for data and Orange colour for power) | [5 empty] | 0 | 0
a. | 250 mm (wide) x 40 mm (height) | RM | 15 | 15 |  |  | 0 | 0
b | 150 mm (wide) x 40 mm (height) | RM | 40 | 40 |  |  | 0 | 0
c | 100 mm (wide) x 40 mm (height) | RM | 25 | 25 |  |  | 0 | 0
[7 empty] | 0 | 0
19 | Fabricating supplying to site of installation, in floor/ceiling including chase cutting of floor,leveling, refilling and making good the same from 1.6 mm thick and 2 mm thick cover pregalvanised MS CRCA sheet, totally enclosed, height 40 mm . The two lengths of raceways shall be fitted with Collars , 50 mm wide, 3 mm thick , press fit type. The raceways shall be clamped to the floor slab with GI clamps , 3mm thick and shall be screwed to the floor slab. The joint between raceway and junction box will be made with GI flexible strip( 3 nos), 3 mm thick, 4 inches long ,15 mm wide which will be nut bolted to the Junction box complete as required etc. | [5 empty] | 0 | 0
a. | 250 mm (wide) x 40 mm (height) | RM | 20 | 20 |  |  | 0 | 0
b | 150 mm (wide) x 40 mm (height) | RM | 40 | 40 |  |  | 0 | 0
c | 100 mm (wide) x 40 mm (height) | RM | 25 | 25 |  |  | 0 | 0
[7 empty] | 0 | 0
20 | Fabricating supplying to site of installation, Junction boxes for floor/ceiling raceways made from 2 mm thick , with 2.5 mm thick G.I power coated cover including providing neoprene gaskets between the cover and the junction box, cadmium plated flat/round head screws, height as per site condition,totally enclosed. Proper cutouts shall be made in the side walls for raceway entry wherever required. The junction box shall be all side walls should be welded expect top cover and all side walls shall have suitable size of rectangular knock out holes for taking raceways / conduits as required and not a complete cut out. The top cover should be sealed with M Seal to make it dust and water proof complete as required etc. | [5 empty] | 0 | 0
a | 300 mm x 300 x 60 mm (height) | Nos. | 5 | 5 |  |  | 0 | 0
b | 200 mm x 200 x 60 mm (height) | Nos. | 6 | 6 |  |  | 0 | 0
c | 150 mm x 150 x 60 mm (height) | Nos. | 8 | 8 |  |  | 0 | 0
d | 100 mm x 100 x 60 mm (height) | Nos. | 3 | 3 |  |  | 0 | 0
[7 empty] | 0 | 0
21 | Providing and fixing Underfloor Access Outlets (250 x 250 x 60 - mm 75 compartments 1Trap including providing and fixing of 3 Nos 6 Amps international UPS sockets and 1 nos 16 Amps switch and 3 Nos. RJ-45 data/ voice outlet complete as required. | Nos. | 1 | 1 |  |  | 0 | 0
[7 empty] | 0 | 0
22 | Providing and fixing Underfloor Access Outlets (250 x 250 x 60 - mm 75 compartments 1Trap including providing 2 Nos 6 Amps international UPS/Raw sockets and 2 nos 6 Amps switch complete as required. | Nos. | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
23 | Supply and fixing of the following sizes of thermoplastic moulded plug and socket IEC 309 type in PVC Box of suitable size flush / surface and making connections complete as required. The box shall be IP 44. | [5 empty] | 0 | 0
[7 empty] | 0 | 0
a | 3 pin 16/20 A 1 phase industrial socket with plug top | Nos. | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
b | 3 pin 32 A 1 phase industrial socket with plug top | Nos. | 2 | 2 |  |  | 0 | 0
[7 empty] | 0 | 0
c | 5 pin 32 A 3 phase industrial socket with plug top | Nos. | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
24 | Checking of all workstation raw and UPS sockets with a Check Plug socket tester & Loop Impedance tester for live-neutral reverse, no earth,neutral fault, live earth reverse, neutral earth reverse. The Circuit No. and DB no. label shall be provided on all UPS ,RAW sockets and switchboards with label printer. | W/S | 475 | 475 |  |  | 0 | 0
[7 empty] | 0 | 0
24 | Providing and fixing in position suitable 1.6 mm thick G.I. outlet box for RJ- 45 computer outlet with all fixing accessories as required. | Nos. | 15 | 15 |  |  | 0 | 0
[7 empty] | 0 | 0
25 | Disconnecting ,removing,storing,handling and refixing of existing 2x2 light ,led down light,channel light, suspended light and hanging light fixture refixing as per revised ceiling plan complete with all fixing accessories as required. | Nos. | 10 | 10 |  |  | 0 | 0
[7 empty] | 0 | 0
26 | Disconnecting ,removing,storing,handling and refixing of existing 2x2 light ,led down light,channel light, suspended light and hanging light fixture refixing as per revised ceiling plan complete with all fixing accessories as required. | Nos. | 450 | 450 |  |  | 0 | 0
[7 empty] | 0 | 0
27 | Supply and laying of Data outlet box with RJ-45 Jack including Cat-6e wire in M.S conduit pipe face plate, socket, documentation, ferruling and crimping complete as required etc. | Nos | 15 | 15 |  |  | 0 | 0
[7 empty] | 0 | 0
28 | Disconnecting ,removing and handing over to owner's store the existing electrical items like lights, Smoke Detectors all conduits, wires , cables , cable trays , raceways, switch , sockets, gang boxes ,enclosure DB's and electrical panels etc. However the items are to be verified by PMC before starting the dismantling works. Only in the modification area | LS. | 1 | 1 |  |  | 0 | 0
[7 empty] | 0 | 0
29 | Cleaning of existing false floor raceway at site . | LS. | 1 | 1 |  |  | 0 | 0
[7 empty] | 0 | 0
| TOTAL CARRIED OVER TO SUMMARY | [5 empty] | 0 | 0
[7 empty] | 0 | 0
B | CABLES, MAINS & SUB MAINS & DISTRIBUTION BOARDS. | [5 empty] | 0 | 0
[7 empty] | 0 | 0
1 | Supply and laying, effecting proper connec­tions, testing & commissioning of the following sizes of 1.1 KV armoured/ unarmoured PVC insulated PVC sheathed aluminium /copper conductor cables conforming to IS : 1554 Part I - 1976 with latest amendments laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to sup­ports in an approved manner as required complete with all accessories. | [5 empty] | 0 | 0
[7 empty] | 0 | 0
a | 3.5 c x 240 sq.mm armoured XLPE insulated aluminium conductor cable | RM | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
b | 3.5 c x 185 sq.mm armoured XLPE insulated aluminium conductor cable | RM | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
c | 4 c x 25 sq.mm armoured XLPE insulated aluminium conductor cable | RM | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
d | 4 c x 16 sq.mm armoured copper conductor cable | RM | 40 | 40 |  |  | 0 | 0
[7 empty] | 0 | 0
e | 2 c x 10 sq.mm armoured copper conductor cable | RM | 25 | 25 |  |  | 0 | 0
[7 empty] | 0 | 0
f | 1c x 50 sq.mm PVC insulated PVC flexible copper conductor cables | RM | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
g | 1c x 35 sq.mm PVC insulated PVC flexible copper conductor cables | RM | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
h | 1c x 16 sq.mm FR PVC insulated flexible copper conductor cables | RM | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
i | 1c x 25 sq.mm FR PVC insulated flexible copper conductor cables | RM | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
j | 4 c x 6 sq.mm armoured copper cable | RM | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
k | 4 c x 4 sq.mm armoured copper cable | RM | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
l | 3 c x 6 sq.mm armoured copper cable | RM | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
2 | Supplying and making terminal joints for the following size of 1.1 KV PVC insulated copper conductor armoured cables including providing heavy duty copper terminal crimping lugs, solder, insulation tape, approved sealing epoxy compound, double compression brass cable glands, effecting gland connec­tions and effecting terminal connections to the equipment complete as required. | [5 empty] | 0 | 0
[7 empty] | 0 | 0
a | 3.5 c x 240 sq.mm armoured XLPE insulated aluminium conductor cable | Jt. | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
b | 3.5 c x 185 sq.mm armoured XLPE insulated aluminium conductor cable | Jt. | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
c | 4 c x 25 sq.mm armoured XLPE insulated aluminium conductor cable | Jt. | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
d | 4 c x 16 sq.mm armoured copper conductor cable | Jt. | 2 | 2 |  |  | 0 | 0
[7 empty] | 0 | 0
e | 2 c x 10 sq.mm armoured copper conductor cable | Jt. | 2 | 2 |  |  | 0 | 0
[7 empty] | 0 | 0
f | 1c x 50 sq.mm PVC insulated PVC flexible copper conductor cables | Jt | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
g | 1c x 35 sq.mm PVC insulated PVC flexible copper conductor cables | Jt | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
h | 1c x 16 sq.mm FR PVC insulated flexible copper conductor cables | Jt | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
i | 1c x 25 sq.mm FR PVC insulated flexible copper conductor cables | Jt. | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
j | 4 c x 6 sq.mm armoured copper cable | Jt | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
k | 4 c x 4 sq.mm armoured copper cable | Jt | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
l | 3 c x 6 sq.mm armoured copper cable | Jt | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
3 | Supply and installation of sheet metal enclosed double door 12 way SPN DB, consisting of 8 Nos. 10/20 AMP SP MCB’s controlled by one number 100 mA sensitivity 40 AMPS DP RCCB backed up with 40 Amps DP MCB. For UPS | Nos.. | 1 | 1 |  |  | 0 | 0
[7 empty] | 0 | 0
4 | 10 Way TPN DB, each phase consisting of 8 Nos. 10/20 AMP SP MCB’s and controlled by one number 63 Amps DP MCB for each phase and 1 no. 63 amps 4 pole MCB incomer | Nos.. | 1 | 1 |  |  | 0 | 0
[7 empty] | 0 | 0
5 | 12 Way SPN DB, consisting of 5 Nos. 32 AMP DP MCB’s and controlled by one number 63 Amps D pole MCB. The bus bar should be twin bus bar and provide 100 Amps bus bar link for phase and neutral incoming cable connection | Nos.. | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
6 | Supply & installation of 10 /20 SP MCB in existing Light , Power & UPS DB including all fixing accessories as required. | Nos | 6 | 6 |  |  | 0 | 0
[7 empty] | 0 | 0
7 | Modification/ Additionof following TPN MCB/ MCCB's complete with all fixing accessories in existing UPS/ LIGHT & POWER SDB | [5 empty] | 0 | 0
[7 empty] | 0 | 0
a | 63 Amps FP MCB | Nos | 0 | 0 |  |  | 0 | 0
b | 63 Amps TPN MCCB | Nos | 0 | 0 |  |  | 0 | 0
c | 63 Amps DP MCB | Nos | 1 | 1 |  |  | 0 | 0
c | 63/40 Amps DP RCCB | Nos | 6 | 6 |  |  | 0 | 0
[7 empty] | 0 | 0
8 | In the existing DBs - Lighting , Raw power and UPS making new/existing connections. testing and commissioning of all existing sockets , DB Dressing, load balancing , making DB charts, checking of existing condition complete as required . | Nos. | 6 | 6 |  |  | 0 | 0
[7 empty] | 0 | 0
9 | Thermal scanning of all the cable and wiring joints in all the panels and MCB Distribution Baords after commissioning . | LS | 1 | 1 |  |  | 0 | 0
[7 empty] | 0 | 0
10 | Supply, installation, testing and commissioning of weather proof enclosures fitted with 32/25/16 A TPN RCBO with ( 300 mA) for VRV | Nos. | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
11 | Supply, installation, testing and commissioning of weather proof polycarbonate enclosures fitted with 32 A FP MCB for A.C. | Nos. | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
12 | Providing as built drawings of electrical & LV system services, as per site condition with 3sets of hard copy and soft copy in pen drive with complete as required etc. | Nos. | 1 | 1 |  |  | 0 | 0
[7 empty] | 0 | 0
13 | Providing and fixing in position the following copper/GI strips and wires including providing all fixing accessories and effecting proper connections | [5 empty] | 0 | 0
[7 empty] | 0 | 0
a. | G.I. tape 25 mm x 6 mm | RM | 0 | 0 |  |  | 0 | 0
c. | Copper wire 8 Cu | RM | 110 | 110 |  |  | 0 | 0
d. | Copper wire 12 Cu | RM | 40 | 40 |  |  | 0 | 0
[7 empty] | 0 | 0
14 | Supply & laying, effecting proper connec­tions, testing & commissioning of the following sizes of 1.1 KV PVC insulated PVC sheathed copper conductor cables conforming to IS : 694/1990 with latest amendments laid over MS supports in existing RCC ducts/ laid in ground /laid on Cable Trays including clamping the cables to sup­ports in an approved manner as required complete with all accessories. | [5 empty] | 0 | 0
[7 empty] | 0 | 0
a. | 1c x 10 sq.mm PVC insulated PVC flexible copper conductor cables (For Server &UPS Earthing ) | RM | 40 | 40 |  |  | 0 | 0
b | 1 x 6 Sq. mm PVC insulated PVC flexible copper conductor cables (Green Colour) | RM | 20 | 20 |  |  | 0 | 0
[7 empty] | 0 | 0
14 | Supplying and making terminal joints for the following size of 1.1 KV PVC insulated copper conductor armoured cables including providing heavy duty copper terminal crimping lugs, solder, insulation tape, approved sealing epoxy compound, brass cable glands, effecting gland connec­tions and effecting terminal connections to the equipment complete as required. | [5 empty] | 0 | 0
[7 empty] | 0 | 0
a | 1Rx 1C x 10 Sq. mm PVC insulated PVC flexible copper conductor cables (Green Colour) | Jt | 4 | 4 |  |  | 0 | 0
[7 empty] | 0 | 0
| TOTAL CARRIED OVER TO SUMMARY | [5 empty] | 0 | 0
[7 empty] | 0 | 0
C | FIRE DETECTION SYSTEM (ANALOGUE ADDRESSABLE) | [5 empty] | 0 | 0
| Make shall be as per existing | [5 empty] | 0 | 0
[7 empty] | 0 | 0
1 | Supply, installation, connecting, testing and commissioning of addressable photoelectric type Smoke Detectors with mounting base, blinking LED etc. complete as required. As per existing make. | Nos | 5 | 5 |  |  | 0 | 0
[7 empty] | 0 | 0
2 | Supply, installation, connecting, testing and commissioning of addressable rate of rise cum fixed temperature Heat Detectors with mounting base, blinking LED etc. complete as required.As per existing make. | Nos | 2 | 2 |  |  | 0 | 0
[7 empty] | 0 | 0
3 | Supply, installation, connecting, testing and commissioning of Addressable Hooters cum strobe min. 95 db output As per existing make. | Nos | 1 | 1 |  |  | 0 | 0
[7 empty] | 0 | 0
4 | Supply, installation, connecting, testing and commissioning of Addressable Manual Call Box in ABS plastic as required complete.As per existing make. | Nos | 1 | 1 |  |  | 0 | 0
[7 empty] | 0 | 0
5 | Supply, installation, connecting, testing and commissioning of addressable fault Isolator.As per existing make. | Nos | 1 | 1 |  |  | 0 | 0
[7 empty] | 0 | 0
6 | Supply, installation, connecting, testing and commissioning of addressable control module for A.C. & Access Control System.As per existing make. | Nos | 1 | 1 |  |  | 0 | 0
[7 empty] | 0 | 0
7 | Supply, installation, connecting, testing and commissioning of addressable control module for Builder AHU and Flow switch.As per existing make. | Nos | 1 | 1 |  |  | 0 | 0
[7 empty] | 0 | 0
8 | Supply, installation, connecting, testing and commissioning of addressable control module Hooter .As per existing make. | Nos | 1 | 1 |  |  | 0 | 0
[7 empty] | 0 | 0
9 | Supply, installation, connecting, testing and commissioning of addressable monitor module for integration of builder panel to main fire panel .As per existing make. | Nos | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
10 | Supply, installation, connecting, testing and commissioning of Response indicator. As per existing make. | Nos | 5 | 5 |  |  | 0 | 0
[7 empty] | 0 | 0
11 | Supply, installation, connecting, testing and commissioning of 2 Loop multiprotocol analog addressable panel ( networkable type ) with auto dialer ( min. 6 line), serial printer and ground isolator card for printer etc. complete as required. As per existing make. | Set | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
12 | Providing and fixing in position the following MS conduits including all accessories concealed in False ceili­ng/walls/partitions as required incl­uding 5 sided 1.5mm thick M.S. junct­ion boxes and 3mm thick perspex sheet cover plate comp­lete with G.I. pull wires. | [5 empty] | 0 | 0
[7 empty] | 0 | 0
a. | 1.6mmwall thickness 20mm dia | RM | 60 | 60 |  |  | 0 | 0
b. | 1.6mm wall thickness 25 mm dia | RM | 110 | 110 |  |  | 0 | 0
[7 empty] | 0 | 0
13 | Providing and fixing in position the following G.I. flexible conduits including all accessories | [5 empty] | 0 | 0
[7 empty] | 0 | 0
a. | 1.6mmwall thickness 20mm dia | RM | 20 | 20 |  |  | 0 | 0
b. | 1.6mm wall thickness 25 mm dia | RM | 10 | 10 |  |  | 0 | 0
[7 empty] | 0 | 0
14 | Supply and drawing of the following FRLS PVC insulated copper conductor wires in existing conduits. | [5 empty] | 0 | 0
[7 empty] | 0 | 0
a. | 2 x 1.5 sq. mm shielded Cu conductor twin core cable | RM | 150 | 150 |  |  | 0 | 0
b. | 2 x 2.5 sq. mm shielded Cu conductor twin core cable | RM | 20 | 20 |  |  | 0 | 0
[7 empty] | 0 | 0
| Note- The existing smoke detector, Hooter, R.I. and fire panel shall be used in the new location as per revised plan. | [5 empty] | 0 | 0
[7 empty] | 0 | 0
15 | Removing and refixing on new location, connecting, testing and commissioning of smoke Smoke Detectors outlet including providing necessary flexible conduit and wires complete as required complete. | Nos | 35 | 35 |  |  | 0 | 0
[7 empty] | 0 | 0
16 | Removing and refixing on new location, connecting, testing and commissioning of Hooter including providing necessary flexible conduit and wires complete as required complete. | Nos | 3 | 3 |  |  | 0 | 0
[7 empty] | 0 | 0
17 | Removing and refixing on new location, connecting, testing and commissioning of smo Manual call point including providing necessary flexible conduit and wires complete as required complete. | Nos | 2 | 2 |  |  | 0 | 0
[7 empty] | 0 | 0
18 | Removing and refixing on new location, connecting, testing and commissioning of R.I point including providing necessary flexible conduit and wires complete as required complete. | Nos | 10 | 10 |  |  | 0 | 0
[7 empty] | 0 | 0
19 | Reprograming the existing panel as required complete. | Nos | 1 | 1 |  |  | 0 | 0
[7 empty] | 0 | 0
| TOTAL CARRIED OVER TO SUMMARY | [5 empty] | 0 | 0
[7 empty] | 0 | 0
D | P.A. SYSTEM | [5 empty] | 0 | 0
| Make shall be as per existing | [5 empty] | 0 | 0
1 | Providing and fixing in position the following MS conduits including all accessories concealed in False ceili­ng/walls/partitions as required incl­uding 5 sided 1.5mm thick M.S. junct­ion boxes and 3mm thick perspex sheet cover plate comp­lete with G.I. pull wires. | [5 empty] | 0 | 0
[7 empty] | 0 | 0
a. | 1.6mmwall thickness 20mm dia | RM | 110 | 110 |  |  | 0 | 0
b. | 1.6mm wall thickness 25 mm dia | RM | 40 | 40 |  |  | 0 | 0
[7 empty] | 0 | 0
2 | Providing and fixing in position the following G.I. flexible conduits including all accessories | [5 empty] | 0 | 0
a. | 1.6mmwall thickness 20mm dia | RM | 20 | 20 |  |  | 0 | 0
[7 empty] | 0 | 0
3 | Supply, installation, testing and commissioning of following Philips ( BOSCH) make Music Accessories/Equipments.as per existing floor. | [5 empty] | 0 | 0
[7 empty] | 0 | 0
a. | Ceiling Speaker Unit 6 Watts LHM 0606/10 | Nos. | 3 | 3 |  |  | 0 | 0
b. | 6 Watts wall mounted speaker unit | Nos. | 0 | 0 |  |  | 0 | 0
c. | Power Amplifier, 480 Watts with output transformer etc. complete. | Nos. | 0 | 0 |  |  | 0 | 0
d | System pre-amplifier with suitable size of PA controller, Router, console, call station and call station keypad suitable for 6 Nos. Zone | Nos. | 0 | 0 |  |  | 0 | 0
e | Single DVD player Philips/Samsung. | Nos. | 0 | 0 |  |  | 0 | 0
f | 6 Zone call station | Nos. | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
g | Control Unit (with volume and on/off switch) Philips ( Smooth stepless control, but the control shall be through dimmer switch, the make of which will be same as the make of light control switches ) | Nos. | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
h | Bosch Microphone console | Nos. | 0 | 0 |  |  | 0 | 0
i | Equipment Rack complete with monitor unit, speaker, power supply control etc. Suitable for 2 x 480 watts amplifire system | Nos. | 0 | 0 |  |  | 0 | 0
[7 empty] | 0 | 0
j | Main Termination Box | Nos. | 1 | 1 |  |  | 0 | 0
[7 empty] | 0 | 0
4 | Supply and drawing of 1.5 sq. mm Twin Core shielded Speaker Cable in existing conduit | RM | 140 | 140 |  |  | 0 | 0
[7 empty] | 0 | 0
5 | Removing and refixing on new location, connecting, testing and commissioning of Speaker outlet including providing necessary flexible conduit and wires complete as required complete. | Nos | 16 | 16 |  |  | 0 | 0
| TOTAL CARRIED OVER TO SUMMARY | [5 empty] | 0 | 0

## FIRE
SUMMARY 8TH FLOOR
|  | AUTOMATIC SPRINKLER SYSTEM (Addition Alteration works) |  |  |  | Rs. | 0
|  | FIRE CURTAINS |  |  |  | Rs. | 688500
[6 empty] | Total | 688500
Sl. No | Description | Unit | 8TH Floor | Supply Rate | Installation Rate | Supply Amount | Installation Amount
1 | AUTOMATIC SPRINKLER SYSTEM (Addition Alteration works) |  |  |  |  | 0 | 0
1.1 | Providing, laying, jointing, testing and commissioning pipework for Sprinkler System including including making connection with existing pipework, fixing of pipework on walls, beams, slabs, columns etc. with M. S. supports (duly painted), adjustable hangers, complete in all respects. |  |  |  |  | 0 | 0
| Material: M.S. pipe Class 'C' conforming to IS:1239 for pipes upto 150 mm dia and IS:3589-1991 for pipes above 150 mm dia. |  |  |  |  | 0 | 0
| Fittings: M.S Forged Fittings Upto 50 mm dia pipes suitable for threaded / weldable socketed joints ; Heavy Class MS fittings for pipes above 50 mm dia suitable for butt welding and flanged joints. |  |  |  |  | 0 | 0
| Painting: Pipework shall be painting with two coats of enamel paint of fire red shade over a coat of primer. |  |  |  |  | 0 | 0
| Firestops: For all horozontal and vertical crossings of building structure ( slabs, walls, beams, coloumn etc) pvc pipe sleeves of dia atleast 30 mm more than the dia of the pipe to be passed through shall be fixed in the building structure, the space buitween the the sleeve and the structure shall be made good. The annular space between the pipe and the sleeves shall be sealed (upto a minimum depth 25 mm) with fire resistant acrylic based sealent of approved make and quality. |  |  |  |  | 0 | 0
| Vendor shall submit all the Manufacturing and Test certificates with the delivery of pipes at site. |  |  |  |  | 0 | 0
| a) 150 mm dia pipe | Rmt | 0 |  |  | 0 | 0
| b) 100 mm dia pipe | Rmt | 0 |  |  | 0 | 0
| c) 80 mm dia pipe | Rmt | 0 |  |  | 0 | 0
| d) 65 mm dia pipe | Rmt | 60 |  |  | 0 | 0
| e) 50 mm dia pipe | Rmt | 35 |  |  | 0 | 0
| f) 40 mm dia pipe | Rmt | 25 |  |  | 0 | 0
| g) 32 mm dia pipe | Rmt | 30 |  |  | 0 | 0
| h) 25 mm dia pipe | Rmt | 175 |  |  | 0 | 0
[6 empty] | 0 | 0
1.2 | Providing and fixing of brass body quartzoide bulb type automatic sprinkler heads set to operate at specified temperature of following types. Sprinkler heads shall be complete with deflector.( UL Listed and FM Approved) |  |  |  |  | 0 | 0
| a) Type : Quick Response Type Pendent Sprinklers Size : 15 mm dia Finish: Chrome K-Factor : 80 |  |  |  |  | 0 | 0
| i) Operating Temp. : 68 deg.C. | Nos. | 75 |  |  | 0 | 0
| ii) Operating Temp. : 79 deg.C. | Nos. | 0 |  |  | 0 | 0
| iii) Operating Temp. : 141 deg.C. | Nos. | 0 |  |  | 0 | 0
| b) Type : Quick Response Type Upright Sprinklers Size : 15 mm dia Finish: Chrome K-Factor : 80 |  |  |  |  | 0 | 0
| i) Operating Temp. : 68 deg.C. | Nos. | 0 |  |  | 0 | 0
| ii) Operating Temp. : 79 deg.C. | Nos. | 0 |  |  | 0 | 0
| c) Type : Quick Response Type Sidewall Sprinklers Size : 15 mm dia Finish: Chrome K-Factor : 80 |  |  |  |  | 0 | 0
| i) Operating Temp. : 68 deg.C. | Nos. | 48 |  |  | 0 | 0
[6 empty] | 0 | 0
1.3 | Providing and fixing of concealed pendent sprinkler with white painted cover plate. Sprinkler head set to operate at specified temperature. Sprinkler heads shall be complete with deflector. ( UL Listed and FM Approved) |  |  |  |  | 0 | 0
| b) Type : Quick Response Type Pendent Concealed Sprinklers Size : 15 mm dia Operating Temp. : 68 deg.C. K-Factor-: 80 Operating Temp. of plate. : 57 deg.C. | Nos. | 10 |  |  | 0 | 0
[6 empty] | 0 | 0
1.4 | Removing, Existing sprinkler heads & flexible drops ( as per site Engineer/Drawing). The cost shall be includes for addtional fittings, consumables, MS supports, repainting of pipes and fittings etc, complete in all respect including testing and commissioning.( Note: The existing pendant sprinklers should be dismantled according to drawing and new pendent to be placed at same location or nearby) | Nos. | 185 |  |  | 0 | 0
[6 empty] | 0 | 0
1.5 | Refixing of existing sprinkler head and flexible drop at same loction or nearest ceiling tile after changing the ceiling tiles ( as per site Engineer/Drawing). The cost shall be includes for addtional fittings, consumables, MS supports, repainting of pipes and fittings etc, complete in all respect including testing and commissioning.( Note: The existing pendant sprinklers should be dismantled according to drawing and new pendent to be placed at same location or nearby) | Nos. | 110 |  |  | 0 | 0
[6 empty] | 0 | 0
1.6 | Providing and fixing of following length braided stainless steel (grade AISI 304) flexible tubing ( of Pressure Rating 16 bar min.) suitable for fire sprinkler installation having 1" NPT mail thread inlet and 1/2" NPT female thread outlet. The unit shall be complete with bracket assembly for securly fixing on false ceiling. The product shall be FM Approved. |  |  |  |  | 0 | 0
| a) 1000 MM long | Nos. | 0 |  |  | 0 | 0
| b) 1200 MM long | Nos. | 48 |  |  | 0 | 0
| c) 1500 MM long | Nos. | 75 |  |  | 0 | 0
[6 empty] | 0 | 0
1.7 | Providing and fixing following type of surface rosette for sprinklers, of approved make. ( UL Listed and FM Approved). The rosette shall be power coated of high quality finish as per the Architect`s approval |  |  |  |  | 0 | 0
| a) Captive rosette |  |  |  |  | 0 | 0
| i) for 15 mm dia | Nos. | 233 |  |  | 0 | 0
[6 empty] | 0 | 0
1.8 | Providing and fixing lever operated butterfly valve of nominal pressure rating 16 bar having nickel and chrom platted disc, stainless steel steel shaft, EPDM body lining and of approved make. including a set of MS flanges, required nos. of nut & bolts all complete. |  |  |  |  | 0 | 0
| a) 100 mm dia with lever | Nos. | 0 |  |  | 0 | 0
| b) 150 mm dia with lever | Nos. | 0 |  |  | 0 | 0
[6 empty] | 0 | 0
1.9 | Providing and fixing flanged end Wafer type check valve (non return valve) of Class PN 16, having stainless steel body and disc, trim and spring of approved make, including a set of MS flanges, required nos. of nut & bolts all complete.(for submersible pumps) |  |  |  |  | 0 | 0
| a) 100 mm dia | Nos. | 0 |  |  | 0 | 0
| b) 150 mm dia | Nos. | 0 |  |  | 0 | 0
[6 empty] | 0 | 0
1.1 | Providing and fixing electric flow switch, capable of sensing a minimum of flow of one sprinkler, including making electrical cable termination |  |  |  |  | 0 | 0
| a) For 100 mm dia sprinkler line | Nos. | 0 |  |  | 0 | 0
| b For 150 mm dia sprinkler line | Nos. | 0 |  |  | 0 | 0
[6 empty] | 0 | 0
1.11 | Providing and fixing of nickel plated brass/ nonferrous alloy fullyway ball valve ( minimum working pressure of 20 bar ) with operating handle of approved make.( Note: Existing isolating valve shall be used for making connection with new pipework) |  |  |  |  | 0 | 0
| a) 25 mm dia | Nos | 0 |  |  | 0 | 0
| b) 40 mm dia | Nos | 0 |  |  | 0 | 0
| c) 50 mm dia | Nos | 0 |  |  | 0 | 0
1.12 | Providing and fixing dial type pressure gauge with isolation cock at hydrant station. (FM Approved) |  |  |  |  | 0 | 0
| a) Dial diameter 150 mm and calibration 0-20 kg./sq.cm. | Nos | 0 |  |  | 0 | 0
[6 empty] | 0 | 0
1.13 | Providing and fixing 25 mm dia gunmetal sight glass assembly with built-in test valve and drain valve including making connection with woth the sprinkler line and termination of drain pipe upto nearest external drain ( UL & FM Approved) | Nos | 0 |  |  | 0 | 0
[6 empty] | 0 | 0
1.14 | Dismentling of following sizes existing sprinkler pipework as per site requirement including disconnecting, rejointing of pipes, fittings etc at required level ( as per site Engineer). The cost shall be includes for addtional fittings, consumables, MS supports, repainting of pipes and fittings etc, complete in all respect icluding testing and commissioning. |  |  |  |  | 0 | 0
| a) 150 mm dia pipe | Rm | 0 |  |  | 0 | 0
| b) 100 mm dia pipe | Rm | 0 |  |  | 0 | 0
| c) 80 mm dia pipe | Rm | 5 |  |  | 0 | 0
| b) 65 mm dia pipe | Rm | 5 |  |  | 0 | 0
| c) 50 mm dia pipe | Rm | 10 |  |  | 0 | 0
| d) 40 mm dia pipe | Rm | 10 |  |  | 0 | 0
| e) 32 mm dia pipe | Rm | 10 |  |  | 0 | 0
| f) 25 mm dia pipe | Rm | 20 |  |  | 0 | 0
[6 empty] | 0 | 0
1.15 | Shifting of following sizes existing sprinkler pipework as per site requirement including disconnecting, rejointing of pipes, fittings etc at required level ( as per site Engineer). The cost shall be includes for addtional fittings, consumables, MS supports, repainting of pipes and fittings etc, complete in all respect icluding testing and commissioning. |  |  |  |  | 0 | 0
| a) 150 mm dia pipe | Rm | 0 |  |  | 0 | 0
| b) 100 mm dia pipe | Rm | 0 |  |  | 0 | 0
| c) 80 mm dia pipe | Rm | 5 |  |  | 0 | 0
| b) 65 mm dia pipe | Rm | 5 |  |  | 0 | 0
| c) 50 mm dia pipe | Rm | 10 |  |  | 0 | 0
| d) 40 mm dia pipe | Rm | 10 |  |  | 0 | 0
| e) 32 mm dia pipe | Rm | 20 |  |  | 0 | 0
| f) 25 mm dia pipe | Rm | 25 |  |  | 0 | 0
[6 empty] | 0 | 0
1.16 | Testing and commissiong of exiting pipes including making commissioning, all complet Ppainting, supporting wherever required ( as directed by Site Engineer) | Nos | 2 |  |  | 0 | 0
[6 empty] | 0 | 0
1.17 | Removing and refixing existing Fire Extinguisher as per site engineer | Nos | 30 |  |  | 0 | 0
[6 empty] | 0 | 0
| TOTAL of "Automatic Sprinkler System" carried over to SUMMARY |  | Rs.
[6 empty] | 0 | 0
2 | FIRE CURTAINS |  |  |  |  | 0 | 0
2.1 | "Fire Curtains" with galvanized MS head box, size( 200X200/450mm) powder coated, side guides size( 53x100mm) along with adjustment channels & bottom bars with motors for power up operation with standard battery backup & operated system safe fixed into steel rollers with woven glass fibre fabric, reinforced with stainless steel wire having micronized aluminium polymer coating on each side of the fabric (silver/grey) with the necessary control panel & all installation assemblies & accessories required to complete the installation. The operation shall be suitable for dedicated 240 Volts UPS, 50 Hz AC supply. Complete system shall be tested in accordance with EN 1634-1 (for 120 minutes Integrity & tested at 1000°C) BS 476-22.8 and BS 7346-3. Quoted rate shall include necessary "Emergency Retract Switch" on both sides of the curtain along with necessary control panel housed within the provided false ceiling depth with suitable supports. The approx. sizes are mentioned below . The electrical panel of curtain shall have potentail free contact for connectivity with BMS system |  |  |  |  | 0 | 0
| a) Single Barrel Fire Curtains Size: 1425mm X 3000mm | Nos | 0 | 150000 | 10000 | 0 | 0
| b) Single Barrel Fire Curtains Size: 2300mm X 3000mm | Nos | 1 | 150000 | 10000 | 150000 | 10000
| c) Double/Multi Barrel Fire Curtains Size: 8990mm X 3000mm | Nos | 0 | 487500 | 20000 | 0 | 0
| d) Double/Multi Barrel Fire Curtains (With egress overlap 650mm) Size: 9300mm X 3000mm | Nos | 1 | 487500 | 20000 | 487500 | 20000
| e) Beam sensor | Nos | 2 | 10000 |  | 20000 | 0
| f) Audio visual alarm | Nos | 2 | 500 |  | 1000 | 0
| TOTAL of "Fire Curtains" carried over to SUMMARY |  | Rs. |  |  | 658500 | 30000

## HVAC
PROJECT: EY CORAL 8TH FLOOR
| DATE: 01.07.2024 |  |  |  |  | 0
S. NO | ITEM DESCRIPTION | UNIT | 8TH FLOOR | SUPPLY RATE | INSTALL. RATE | SUPPLY AMOUNT | INSTALLATION AMOUNT
1 | LOW SIDE HVAC WORKS FOR OFFICE SPACES
| EQUIPMENT |  |  |  |  | 0 | 0
| DUCT WORK / AIR TERMINALS |  |  |  |  | 0 | 0
| INSULATION |  |  |  |  | 0 | 0
2 | VAV BOXES |  |  |  |  | 0 | 0
3 | VRV SYSTEM FOR CRITICAL SPACES
| EQUIPMENT |  |  |  |  | 0 | 0
| PIPING |  |  |  |  | 0 | 0
| ELECTRICAL WORKS |  |  |  |  | 0 | 0
4 | HYDROGEN EXHAUST FOR BATTERY ROOM |  |  |  |  | 0 | 0
5 | VRV SYSTEM FOR BACK-UP AIR CONDITIONING
EQUIPMENT
PIPING
ELECTRICAL WORKS
6 | UNDERDECK INSULATION FOR EXPOSED ROOF
7 | AIR PURIFICATION SYSTEM |  |  |  |  | 0 | 0
8 | CHW BASED CS AHUS FOR LIFT LOBBY
EQUIPMENT
| PIPING AND VALVES |  |  |  |  | 0 | 0
| CHW PIPE INSULATION |  |  |  |  | 0 | 0
ELECTRICAL WORKS
9 | DEMAND CONTROL VENTILATION & VFD For AHU & FA FAN |  |  |  |  | 0 | 0
10 | Dismantling , packing, keeping in store , re installation , testing and commissioning of all HVAC components. |  |  |  |  | 0
| TOTAL (HVAC) |  |  |  |  | 0 | 0
| GRAND TOTAL | [5 empty] | 0
1 | EQUIPMENT
INLINE FAN
| Supply, Installation, Testing & Commissioning of inline fans for Exhaust/ Fresh air supply complete with sheet metal casing, 25mm thick open cell nitrile rubber acoustic insulation, direct driven centrifugal fan, motor with proper protection and inspection door. Fan shall be suitable for operation on 220±6 % volts, 50 Hz,1 phase AC power supply. Flanges to be provided on both sides to facilitate duct connections. Fan shall be installed as shown in the drawings and will be of following characteristics : All single phase inline fans shall be provided with factory fitted speed regulators. All Fans Should be complete with Plug Top & necessary power cable. Fans shall have low noise level in rage of 35-40dBA @3m and shall be suitable for indoor installations. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Fan Capacity S.P Area to |  |  |  |  | 0 | 0
| No. (Cfm) (mmWG) to be exhausted |  |  |  |  | 0 | 0
| IF-1 1200 13-14 Toilet / pantry | Nos | 1 |  |  | 0 | 0
| IF-2 750 13-14 Toilet | Nos |  |  |  | 0 | 0
| IF-3 600 13-14 Toilet | Nos |  |  |  | 0 | 0
| IF-4 500 13-14 Toilet | Nos |  |  |  | 0 | 0
| IF-5 400 13-14 Toilet | Nos |  |  |  | 0 | 0
| IF-6 300 13-14 Servery/Prep/Dish/toilet | Nos |  |  |  | 0 | 0
| IF-7 200 13-14 Toilet | Nos |  |  |  | 0 | 0
[6 empty] | 0 | 0
| TOTAL ITEM NO. 1 (EQUIPMENT) |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.0 | DUCTWORK/AIR TERMINALS |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.1 | FACTORY FABRICATED DUCTING |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation and Testing of factory fabricated GSS (class VIII-120GSM Zinc Coaing) ducting complete with vanes, splitter dampers, fire retardant gaskets hanging arrangement including fully threaded GI rods and GI "C" channels/ rolled steel wires or Gripple Wire Rope Hangers & Supports complete with end fixing, GI "C" channels etc. as approved by clients/consultants in accordance with the approved shop drawings and specifications. Quoted price shall be inclusive of necessary scaffolding charges towards installation of supply/exhaust air ducts outside or within building wherever required. Quoted price should also include necessary charges towards duct supporets including MS angle/channel arrangement as required for ducts being installed outside or within building wherever required. |  |  |  |  | 0 | 0
| Spacing between duct supports should not exceed 2m in both cases i.e GI rods with GI "C" channels & Gripple Wire Rope Hanger support. In case of Gripple Wire Rope Hanger support for duct sizes above 1800mm, MS angles duly painted with black enamel paint should be used along with neoprene pad in between the duct & MS angle. All duct support to be provided with check nuts (lock nuts). Duct to be brought at site in Box form. |  |  |  |  | 0 | 0
| While selecting the duct supports vendor shall ensure vibration free installation. Quoted price shall be inclusive of light test or smoke test. Necessary arrangement for testing to be made by HVAC Vendor. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | 1mm to 899mm -- 26G GSS with TDC Joints | SqM | 30 |  |  | 0 | 0
b. | 900mm to 1200mm -- 24G GSS with TDC Joints | SqM | 10 |  |  | 0 | 0
c. | 1201mm to 1800mm - 22G GSS with TDC Joints | SqM |  |  |  | 0 | 0
d. | 1801mm to 2100mm - 20G GSS with TDC Joints | SqM |  |  |  | 0 | 0
e. | 2101mm to 2700mm - 18G GSS with TDC Joints | SqM |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.2 | SITE FABRICATED DUCTING |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Fabrication, Installation and Testing of GS sheet metal (class VIII-120GSM Zinc Coaing) ducts complete with vanes, splitter dampers, hanging arrangement including check nuts in accordance with the approved shop drawings and specifications. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| a. 0.63mm (24 gauge) GSS | SqM | 10 |  |  | 0 | 0
| b. 0.8 mm (22 gauge) GSS | SqM | 10 |  |  | 0 | 0
| c. 1.0mm (20 gauge) GSS | SqM |  |  |  | 0 | 0
| d. 1.25mm (18 gauge) GSS | SqM |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.3 | FLAT OVAL SPIRAL DUCT |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation and Testing of factory fabricated & factory internally insulated GSS (class VIII-120GSM Zinc Coaing) flat oval spiral ducting complete with vanes, splitter dampers, fire retardant gaskets hanging arrangement including fully threaded GI rods, GI straps and GI "C" channels/ rolled steel wires or Gripple Wire Rope Hangers & Supports complete with end fixing, GI "C" channels etc. as approved clients/consultants in accordance with the approved shop drawings and specifications. Quoted price shall be inclusive of necessary scaffolding charges towards installation of supply/exhaust air ducts outside or within building wherever required. |  |  |  |  | 0 | 0
| Insulation material shall be 9mm/13mm thick, food grade material, with antimicrobial properties, Class "O" closed cell elastomeric insulation material. Adhesive should be Fire Retardant, LEED compliant and Low VOC. |  |  |  |  | 0 | 0
| Contractor to involve OEM Expert team for erection of ductwork at site to ensure high quality workmanship of duct joints. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Without Powder Coated-With 13mm thick insulation |  |  |  |  | 0 | 0
| 1mm to 1700mm -- 22G GSS | SqM | 10 |  |  | 0 | 0
[6 empty] | 0 | 0
2.4 | DUCO PAINT (For Flat Oval Exposed Duct) |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply and Application of minimum two coats of Duco Paint of colour and shade as approved by the Architects for exposed flat oval spiral/ round ducts. Quoted price shall be inclusive of primer before paint and all neceesary arrangement as required for providing the paint over duct. Paint to be applied using spray guns properly for uniform & smooth finish. | SqM | 10 |  |  | 0 | 0
[6 empty] | 0 | 0
2.5 | FLEXIBLE CANVASS CONNECTIONS |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing of 125mm deep antivibration flexible joints at the outlet of air handling units/ductable split units//inline fans. Flexible connections shall be constructed using imported fire retardant fabric with extruded aluminium frame/flange on both sides of approved make. | Rmt | 20 |  |  | 0 | 0
[6 empty] | 0 | 0
2.6 | LINEAR GRILLES |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Balancing of one way blow linear supply cum return air grilles complete with fixed core as per approved shop drawings and specifications. The grilles shall be of approved colour & shade. |  |  |  |  | 0 | 0
| Powder coated aluminium grilles of extruded sections with integral flanges on both sides & ends as required complete with corner pieces. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| i. 100/150/200/250 mm/600mmx600mm Grilles | SqM | 5 |  |  | 0 | 0
[6 empty] | 0 | 0
2.7 | CURVED GRILLES |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Balancing of one way blow linear curved supply air grilles complete with fixed core as per approved shop drawings and specifications. The grilles shall be of approved colour & shade. |  |  |  |  | 0 | 0
| Powder coated aluminium grilles of extruded sections with integral flanges on both sides & ends as required complete with corner pieces. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| i. 100/150/200/250 mm High grilles | SqM | 2 |  |  | 0 | 0
[6 empty] | 0 | 0
2.8 | DOUBLE LOUVERED GRILLES |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Balancing of double louvered supply air grilles as per approved shop drawings and specifications complete with key operated aluminium volume control dampers. |  |  |  |  | 0 | 0
| a. Powder coated extruded aluminiu grilles. | SqM | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
2.9 | AIR TRANSFER GRILLES |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation and Testing of extruded aluminium powder coated air transfer grilles to be provided at the door of toilets/pantry. | SqM | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
2.1 | ROUND DIFFUSERS |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Balancing of round supply air diffusers with removable key operated butterfly volume control dampers as per the approved shop drawings and specifications. The diffusers shall be anti-smudge flush type as approved by the interior designer. Diffuser shall be complete with GI cone with circular connection at the rear. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Powder coated extruded aluminium diffusers of approved colour & shade suitable for fixing in exposed duct or in grid/gypsum ceiling as per approved shop drawing. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.10.1 | With Volume Control Dampers |  |  |  |  | 0 | 0
a. | 250mm dia Neck Size round diffuser with GI cone | Nos | 5 |  |  | 0 | 0
b. | 150mm dia Neck Size round diffuser with GI cone | Nos |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.10.2 | Without Volume Control Dampers |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | 250mm dia Neck Size round diffuser with GI cone | Nos | 5 |  |  | 0 | 0
b. | 200mm dia Neck Size round diffuser with GI cone | Nos |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.11 | SUPPLY AIR DIFFUSERS |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.11.1 | Supply, Installation, Testing and Balancing of square supply air diffusers with removable key operated volume control dampers with opposed blades as per the approved shop drawings and specifications.The diffusers shall be anti-smudge ring type/flat type as approved by the interior designer. Diffusers shall be with removable core for the following neck sizes. The diffusers shall be suitable for fixing in the gypsum/grid ceiling. The diffusers shall be of regular type and with outer dimension of 600mm x 600mm, 450 x 450mm, 375mmx375mm & 300mmx300mm. |  |  |  |  | 0 | 0
| Powder coated extruded aluminium diffusers of approved colour & shade. | SqM | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
2.12 | RETURN AIR DIFFUSERS |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.12.1 | Supply, Installation,Testing and Balancing of square return air diffusers same as supply air diffusers but without volume control dampers as per the approved shop drawings and specifications. The diffusers shall be anti -smudge ring type. All Return air diffusers in false ceiling to be properly supported from real slab using chains or gripple wires. |  |  |  |  | 0 | 0
| Powder coated extruded aluminium diffusers of approved colour & shade. | SqM | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
2.13 | Supply, Installation, Testing and Balancing of Powder coated extruded aluminium Plaque diffusers as per the approved shop drawings as per the specifications. All Return air diffusers in false ceiling to be properly supported from real slab using chains or gripple wires. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | 600x600 size diffusers with spiggot to facilitate round flexible duct connections for supply air but without VCD. Diffusers shall be complete with plenum as per specifications and complete with removable plate. | Nos | 2 |  |  | 0 | 0
[6 empty] | 0 | 0
b. | 600x600 size diffusers with VCD. Diffusers shall be complete with plenum as per specifications and complete with removable plate. | Nos | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
c. | 600x600 size diffusers without spigot for return air. Diffusers shall be without VCD and provided with fixed plate. | Nos | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
2.14 | Supply, Installation, Testing and Balancing of linear slot diffusers as per the approved shop drawings and specifications. Each slot shall be 25mm wide. The diffuser face shall be a one piece extrusion so there are no visible joints. Slot diffusers shall be complete with end caps either as end plates or end angles or integral part, air control blades etc. Slot diffuser have a variable neck length and the diffuser face could be optionally be fitted to the plenum box on site. Diffuser shall have provision to access collar dampers for air balancing. |  |  |  |  | 0 | 0
| Sample & color of Diffusers to be got approved from Clients/Architects befor procurement. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | 3 slot/2slot, powder coated extruded aluminium diffusers of approved colour & shade. | SqM | 0.5 |  |  | 0 | 0
b. | 3 slot/2slot, powder coated extruded aluminium diffusers of approved colour & shade for supply air with Hit & Miss type dampers. | SqM | 0.5 |  |  | 0 | 0
[6 empty] | 0 | 0
2.15 | Supply, Installation, Testing and Balancing of flexible ducting comprising of inner as well as outer skin constructed out of aluminium & fibre glass insulation 25mm thick of minimum 24 kg/cu.m density insulation sandwitched in between. Duct should confirm to fire rating standards BS-476 part 5, 6 & 7. Flexible Ducts of following sizes as per approved shop drawings, specifications : Universal (Jubilee) clamp should be provided to fix the flexible duct in the spigots/Butterfly Dampers and covered with aluminium tape. Circular clip with chain/GI threaded rod to be provided to support the flexible duct. |  |  |  |  | 0 | 0
a. | 300 mm dia | Rmt |  |  |  | 0 | 0
b. | 250 mm dia | Rmt | 10 |  |  | 0 | 0
c. | 200 mm dia | Rmt | 10 |  |  | 0 | 0
d. | 150 mm dia | Rmt | 5 |  |  | 0 | 0
e. | 100 mm dia | Rmt |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.16 | Supply, Installation and Testing of single piece GI round spigot made out of spinning process with 50mm height and having grooves on both sides and circular flanges. Spigots shall be installed on main ducts to facilitate connection of flexible ducts. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | 300 mm dia | Nos | 0 |  |  | 0 | 0
b. | 250 mm dia | Nos | 5 |  |  | 0 | 0
c. | 200 mm dia | Nos | 5 |  |  | 0 | 0
d. | 150 mm dia | Nos | 5 |  |  | 0 | 0
e. | 100 mm dia | Nos |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.17 | Supply, Installation and Testing of Butterfly damper of GI sheet construction with two flap with round flange on one side and 10mm grove on other side for fixing of flexible duct with the help of band, 20 Gauge Frame 250mm dia & above, 22 Gauge Frame upto 200mm dia & 22 Gauge Blade in all sizes as per thespecifications and shop drawings. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | 300 mm dia | Nos |  |  |  | 0 | 0
b. | 250 mm dia | Nos | 5 |  |  | 0 | 0
c. | 200 mm dia | Nos | 5 |  |  | 0 | 0
d. | 150 mm dia | Nos | 5 |  |  | 0 | 0
e. | 100 mm dia | Nos |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.18 | Supply, Installation and Testing of GI box type volume control dampers as per the specifications and shop drawings. - For Rectangular Ducts | SqM | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
2.19 | Supply, Installation and Testing of GI box type volume control dampers as per the specificationsand shop drawings. - For Flat Oval Ducts | SqM |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.2 | Supply, Installation and Testing of Aluminium multi blade type louver dampers as per the specifications and shop drawings of approved colour & shade. | SqM | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
2.21 | Supply, Installation, Testing and Commissioning of motorised fire dampers suitable for at least 120 minutes fire rating as per the specifications and approved shop drawings. Quoted price shall be inclusive of copper control wiring & Power cabling as required. |  |  |  |  | 0 | 0
| Fire dampers shall be provided with 450 mm sleeves suitable for the wall mounting. (Sleeve Thickness -1.2mm) |  |  |  |  | 0 | 0
a. | Bare Fire Dampers | SqM | 3 |  |  | 0 | 0
b. | Spring return action type actuator complete with control panel and temperature sensor. Torque not less than 16NM. Actualtor shall be BMS Compatible. | Nos | 5 |  |  | 0 | 0
[6 empty] | 0 | 0
2.22 | Supply, Installation and Testing of multiblade box type zero leakage extruded aluminium dampers for ducts to be provided with suitable links, levers and quadrants for manual control of volume of air flow and for proper balancing of the air distribution system as per the approved shop drawing and specifications. | SqM | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
2.23 | Supply and fixing of actuators complete with control panel of suitable rating of torque complete with copper wiring from the junction box and actuator associated with the above VCDs. |  |  |  |  | 0 | 0
| Bare Fire Dampers | SqM |  |  |  | 0 | 0
| Actuator shall be suitable for duct size as shown in the drawing. | Nos |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.24 | Supply, Installation and Testing of Louver with Bird Screens with GI wire mesh to be installed at the suction of fresh air/discharge of Exhaust air as per the specifications and shop drawings. Sample of bird screen to be got approved from consultants and Clients prior to procurement. | SqM | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
2.25 | Supply, Installation and Testing of non return dampers. NRDs to be installed in the ducts as per the specifications and shop drawings. Sample of NRDs to be got approved from consultants and Clients prior to procurement. | SqM | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
2.26 | FACTORY FABRICATED PLENUMS |  |  |  |  | 0 | 0
| Supply, Installation and Testing of 25mm thick factory fabricated double skin plenum having specifications same as existing double skin air handling units. Inner skin shall be constructed out of 24 gauge plain GS sheet & outer skin in 24 gauge pre-plasticized GS sheet sandwiched between 25mm thick injected PU foam insulation of density not less than 40 Kg /CuM and complete with inspection doors as required. Plenum shall be installed at AHU outlet having following sizes or as per approved shop drawing. Supply air flanged openings in the plenum should be as per approved shop drawing. Plenum shall be acoustically lined with 10mm open cell nitrile rubber insulation. Vendor to check actual AHU size at site and quote accordingly. |  |  |  |  | 0 | 0
| Vendor to ensure that Plenum size & Openings should strictly be based on actual AHU size at site and as per approved shop drawing. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | For Floor Mounted AHU | SqM | 0 |  |  | 0 | 0
[6 empty] | 0 | 0
2.27 | RETURN AIR BAFFLE WITH INTERNAL ACOUSTIC INSULATION |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation and Testing of Z - shaped factory fabricated Return air Baffles constructed out of 22G GSS (class VIII-120GSM Zinc Coaing) complete with 15mm thick internal acoustic lining on four sides using open cell nitrile rubber insulation. 22G GSS sheet duly acoustically lined on both sides using 10mm open cell nitrile rubber insulation to be provided as Vane/splitter in between of baffle. Insulation density to be within 140-180 Kg/m3 and Insulation material shall be bonded with the ducts using Fire Retardant, LEED compliant and Low VOC adhesive. Metal screw and washers to be provided to facilitate grip to the GI sheet. |  |  |  |  | 0 | 0
| Quoted price shall be inclusive of hanging arrangement including fully threaded GI rods and GI "C" channels/ rolled steel wires or Gripple Wire Rope Hangers & Supports complete with end fixing, GI "C" channels etc. as approved by clients/consultants in accordance with the approved shop drawings and specifications. Quoted price shall be inclusive of necessary scaffolding charges towards installation within building wherever required. | SqM | 5 |  |  | 0 | 0
| Note: Calculation based on Perimeter basis: (W+H)x2xL |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| TOTAL ITEM NO.2 (Ducting & Air Terminals) |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
3.0 | INSULATION |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
3.1 | ACOUSTIC LINING OF DUCTS |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
3.1.1 | Using Open Cell Nitirile Rubber |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply and Application of internal acoustic lining of supply air ducting using open cell nitrile rubber insulation with density within 140-180 Kg/m3 as per the approved shop drawings and specifications. Insulation material shall be bonded with the ducts using metal screw and washers to facilitate grip to the GI sheet. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | 15mm thick lining | SqM | 10 |  |  | 0 | 0
[6 empty] | 0 | 0
3.2 | THERMAL INSULATION OF DUCTS |  |  |  |  | 0 | 0
| (Using aluminium foil faced Class 'O' Fire Retardant Properties Closed Cell Elastomeric insulation) |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply and Application of external thermal insulation of supply /return air ducting using factory laminated aluminium foil faced closed cell elastomeric nitrile rubber insulation with class 'O' fire retardant properties as per the specifications and drawings. Cladding shall provide protection from mechanical impact, and Scratches etc. Both insulation & cladding should have built in antimicrobial protection. Adhesive - AC Duct King Eco Fresh |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | 13mm thick insulation-S/A Ducts & R/A ducts Non AC Areas | SqM | 50 |  |  | 0 | 0
b. | 16mm thick insulation - For S/A Duct in Non AC Area & Fresh Air Duct | SqM |  |  |  | 0 | 0
[6 empty] | 0 | 0
3.3 | ACOUSTIC LINING OF AHU ROOMS |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply and Application of acoustic/ thermal lining of walls/ ceiling of AHU rooms using resin bonded fibre glass insulation of density not less than 32Kg/CuM as per the approved shop drawings and specifications. Quoted price shall be inclusive of GSS channel, metal screws, washers, fibre glass tissue, perforated aluminium sheet of 24G etc. as required for complete installation. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | 50mm thick lining | SqM |  |  |  | 0 | 0
[6 empty] | 0 | 0
| TOTAL ITEM NO. 3 (INSULATION) |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
SECTION 'B' - VAV BOXES | [5 empty] | 0 | 0
[6 empty] | 0 | 0
1 | POTENTIOMETER FOR AHUs - IN CASE NOT PROVIDED BY DEVELOPERS |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Potentiometer for AHUs with EC Fans to control EC Fans based on DPS/ Temp. sensor command. Internal wiring in AHU & wiring from DPS/Temp. sensor to Potentiometer to be considered as per system's requirement. Operating Range of signal shall be 4 mA to 20 mA OR 0 V to 10 V DC similar to DPS for variable speed operation of EC Fans. | Nos | 0 |  |  | 0 | 0
[6 empty] | 0 | 0
2 | VAV BOXES RECTENGULAR SHAPE (ONLINE TYPE) |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Commissioning of On Line type variable air volume boxes complete with necessary controllers, Heating-Cooling digital thermostat, Damper actuator, multi point pick-up inlet Air Flow velocity sensor and copper control wiring and necessary transformer etc. as required and as per the specifications. VAV Boxes shall be BMS compatible. VAV Boxes should be suitable to working on Cooling & Heating mode as per requirement. VAV Box shall be of following design parameters : |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Max. Air Qty. Min. Air Qty. Location |  |  |  |  | 0 | 0
| (Cfm) (Cfm) |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | Upto 500 50 As shown on Drg. | Nos | 2 |  |  | 0 | 0
b. | From 525 to 1000 From 50 to 100 As shown on Drg. | Nos | 1 |  |  | 0 | 0
c. | From 1025 to 1500 From 100 to 150 As shown on Drg. | Nos | 1 |  |  | 0 | 0
d. | From 1525 to 2000 From 150 to 200 As shown on Drg. | Nos | 2 |  |  | 0 | 0
e. | From 2025 to 2500 From 200 to 250 As shown on Drg. | Nos |  |  |  | 0 | 0
f. | From 2525 to 3000 From 250 to 300 As shown on Drg. | Nos |  |  |  | 0 | 0
g. | From 3025 to 3500 From 300 to 350 As shown on Drg. | Nos |  |  |  | 0 | 0
h. | From 3525 to 4000 From 350 to 400 As shown on Drg. | Nos |  |  |  | 0 | 0
[6 empty] | 0 | 0
3 | VAV BOXES -OVAL SHAPE (ONLINE TYPE) |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Commissioning of Oval Shaped On Line type variable air volume boxes complete with necessary controllers, Heating-Cooling digital thermostat, Damper actuator, multi point pick-up inlet Air Flow velocity sensor and copper control wiring and necessary transformer etc. as required and as per the specifications. VAV Boxes shall be BMS compatible. VAV Boxes should be suitable to working on Cooling & Heating mode as per requirement. VAV Box shall be of following design parameters : |  |  |  |  | 0 | 0
| VAV should be integrated with in the ducts i.e. VAV Size should be same as of Duct it would be installed in. VAV Controller shall be within VAV casing. It shouldn't be visible from outside. |  |  |  |  | 0 | 0
| Max. Air Qty. Min. Air Qty. Location |  |  |  |  | 0 | 0
| (Cfm) (Cfm) |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | Upto 500 50 As shown on Drg. | Nos |  |  |  | 0 | 0
b. | From 525 to 1000 From 50 to 100 As shown on Drg. | Nos |  |  |  | 0 | 0
c. | From 1025 to 1500 From 100 to 150 As shown on Drg. | Nos |  |  |  | 0 | 0
d. | From 1525 to 2000 From 150 to 200 As shown on Drg. | Nos |  |  |  | 0 | 0
e. | From 2025 to 2500 From 200 to 250 As shown on Drg. | Nos |  |  |  | 0 | 0
f. | From 2525 to 3000 From 250 to 300 As shown on Drg. | Nos |  |  |  | 0 | 0
g. | From 3025 to 3500 From 300 to 350 As shown on Drg. | Nos |  |  |  | 0 | 0
h. | From 3525 to 4000 From 350 to 400 As shown on Drg. | Nos |  |  |  | 0 | 0
[6 empty] | 0 | 0
4 | DUCT PRESSURE SENSORS |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation and Testing of pressure sensors to be installed in supply air ducts. Quoted price shall be inclusive of necessary conduting, copper control cabling from the sensors to the respective VFDs as per "Approved Shop Drawings". | No | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
5 | CONTROLLER FOR BACNet INTEGRATION |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
5.1 | Supply, Installation and Testing of controller for BACNet integration above VAV Boxes with BMS. Controller should be suitable to be integrated with minimum 70Nos. of VAV Boxes. Integrator shall be capable of soft integration with BMS system. | No | 1 |  |  | 0 | 0
5.2 | Supply, laying, affecting connections and Testing of all necessary copper control wiring/ daisy chain cabling etc. as required for proper functioning & integration of VAVs with above controller. All cabling to be laid in MS conduits. Quoted price shall be inclusive of all necessary arrangement to make system complete & functional.VAV Unit to Thermostat | RM | 100 |  |  | 0 | 0
5.3 | Supply, laying, affecting connections and Testing of all necessary copper control wiring/ daisy chain cabling etc. as required for proper functioning & integration of VAVs with above controller. All cabling to be laid in MS conduits. Quoted price shall be inclusive of all necessary arrangement to make system complete & functional. All Thermostat to AHU Room for Controlling | RM | 100 |  |  | 0 | 0
[6 empty] | 0 | 0
| TOTAL -VAVs |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
SECTION 'C' - VRV SYSTEM FOR CRITICAL SPACES | [5 empty] | 0 | 0
[6 empty] | 0 | 0
1.0 | EQUIPMENT |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
1.1 | VARIABLE REFRIGERANT VOLUME SYSTEM |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Commissioning of Variable Refrigerant Volume type multi unit air-conditioning system complete with indoor and outdoor units with individual controller for cooling application as per the specifications and drawings. The quoted price should include clearances charges, local taxes, freight etc. Quoted price shall also be inclusive of loading, unloading, lifting & shifting on outdoor location in space available at same floor level or at terrace at suitable locations as per drawing, positioning charges besides including charges towards structural steel supports, MS base frame duly painted & vibration isolation arrangement etc. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
1.1.1 | OUTDOOR UNITS |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Commissioning of air cooled variable refrigerant flow modular type Outdoor units, each comprising of energy efficient multiple scroll compressors, full charge of R-410a refrigerant gas and all accessories as per the specifications. All compressors shall be inverter type. The condensing units shall be suitable to work on cooling mode even during peak winters. The condensing units shall be suitable for operation on 415 ±10% volts, 50Hz, 3 phase AC power supply and complete with auto check function for connection error, auto address setting, etc. The outdoor units shall be low noise type. Quoted price shall be inclusive of Power Cable from MCCB to Outdoor unit & MS frame duly applied with 2 coat of primer & one coat of black enamel paint. The outdoor units shall be of following capacities : |  |  |  |  | 0 | 0
| Quoted price shall be inclusive of factory applied epoxy coating (to prevent erosion of tubes & fins) of Outdoor units. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| VRV ODUs shall be capable of operating in following range : i. For Cooling : (-)5degC to 50degC |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
i | 28HP (12+16) nominal capacity high COP outdoor unit Cooling Mode Only | No |  |  |  | 0 | 0
ii | 24HP (12+12) nominal capacity high COP outdoor unit Cooling Mode Only | No |  |  |  | 0 | 0
iii | 8HP nominal capacity high COP outdoor unit | No |  |  |  | 0 | 0
iv | 10 HP nominal capacity high COP outdoor unit | No |  |  |  | 0 | 0
[6 empty] | 0 | 0
1.1.2 | INDOOR UNITS |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Commissioning of variable refrigerant volume modular type indoor units comprising of EEV & all accessories as per the specifications. The indoor units shall be suitable to work on cooling as well as heating mode. The indoor units shall be suitable for operation on 220 ±6% volts, 50Hz, 1 phase AC power supply. Ductable indoor units shall be suitable to handle extent of ductwork as shown in the design drawings and dehumidified air quantity as mentioned in the heat load summary sheet under "Special Conditions" and the indoor units shall be of following capacities. All Indoor Units (except Wall mounted type units) shall have inbuilt Drain Pumps. Ductable Units shall have provision of interlocking with Motorized Dampers for Working/Standby Mode. Quoted price shall be inclusive of Plug Top & necessary power cable. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
i. | 2800 CFM Ductable Type (8.0 TR) | No. |  |  |  | 0 | 0
ii. | 2200 CFM Ductable Type (6.4 TR) | No. |  |  |  | 0 | 0
iii. | 1130 CFM Ductable Type (3.2 TR) | No. |  |  |  | 0 | 0
iv | 459 CFM Hi-Wall Type (1.3 TR) | No. |  |  |  | 0 | 0
v | 530 CFM Hi-Wall Type (1.6 TR) | No. |  |  |  | 0 | 0
vi | 670Cfm Wall Mounted Type (2.0TR) | No. |  |  |  | 0 | 0
Vii | 512 CFM Compact Cassette Type (1.6 TR) With Drain Pump | No. |  |  |  | 0 | 0
[6 empty] | 0 | 0
1.2 | REMOTE CONTROLS |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
i | Supply, Installation, Testing & Commissioning of Corded remote controls for the above indoor units. | No |  |  |  | 0 | 0
[6 empty] | 0 | 0
1.3 | CENTRALISED CONTROLLER |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Commissioning of main Intelligent Touch Manager with plus adapter as per specifications to hook up indoor units as mentioned above. Controller shall however, be suitable for minimum 128 groups of indoor units. Centralized controller shall act as master controller for controlling of cooling mode of outdoor units and their associated indoor units. Controller shall be suitable of Remote Access with computer and shall have web access. Controller shall be suitable to autosequence the outdoor as well as indoor units catering to 24x7 operated areas as required. Controller shall be suitable to configured the inside temperature as per temperature set point on controller. Controller shall have time schedulling arrangement for Indoor Units as well as Outdoor Units. Controller shall be BMS Compatible with Modbus RS 485 communication protocol. Controller shall be complete with all accessories required for soft integration to BMS system Quoted price shall be inclusive of all necessary cabling as required from ODU & IDUs to controller. Centralized controller shall be common for all VRV units including Back-up AC units. Price to be quoted accordingly. | No |  |  |  | 0 | 0
[6 empty] | 0 | 0
1.4 | DRAIN PUMP |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing & Commissioning of On Line Type Condensate drain pump for Hi-wall units complete with water level sensor and accessories as required. Quoted price shall be inclusive of controller, NRVs & water sensors and associated wiring etc. to make installation complete. Drain Pump shall be suitable for operation on 220+6 % volts 50 Hz, 1phase AC power supply. |  |  |  |  | 0 | 0
| Drain pumps shall automatically ON/Off based on water level. |  |  |  |  | 0 | 0
| Apsen- MAX Hi Flow |  |  |  |  | 0 | 0
a. | Drain pump for Ductable units & Hi-Wall Split Unit | Nos. | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
1.5 | Supply & Installation of GI Drain tray duly insulated with 13mm thick closed cell elastomeric insulation with class 'O' fire retardant properties below Hi wall Split Units in Technical Spaces. Trays to be provided below Hi wall units coming over panels or other Equipments. Drain tray to be connected with drain piping. | Nos. | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
1.6 | Supply, Installation, Testing and Commissioning of Temperature Sensor with Digital Display & Alarm in form of light (or Sound as required by Clients) etc. Alarm should be raised as soon as there is temperature fluctuation from Set temperature. Alarm needs to be installed outside Server Room. Quoted Price shall be inclusive of Power & Control cabling and Integration as required. | Lot |  |  |  | 0 | 0
[6 empty] | 0 | 0
| TOTAL ITEM NO. 1 (EQUIPMENT) |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.0 | PIPING |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.1 | COPPER REFRIGERANT PIPING |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing & Commissioning of high pressure copper refrigerant piping including R410a refrigerant of suitable size as required and duly insulated with19mm/13mm thick closed cell elastomeric insulation with class 'O' fire retardant properties with IC Cladding in tubing form. External Refrigerant piping shall be laid on GI covered ladder type cable trays. Piping inside occupied spaces shall be supported using MS hangers duly painted with black enamel paint. Entire refrigerant piping work shall be carried out in accordance with the specifications.MS sleeves of requisite size shall be provided at wall crossing. Quoted price shall be inclusive of necessary glass cloth and minimum two layers of UV protection paint to be applied over insulation for all exposed pipes of approved make. Piping shall be of following sizes : |  |  |  |  | 0 | 0
| Internal Refrigerant piping in exposed ceiling area & external refrigerant piping shall be laid on Ladder type cable trays. Cable trays used for external refrigerant piping shall be covered with GI cover. |  |  |  |  | 0 | 0
| The copper refrigerant piping and all other exposed copper components shall be provided with Polysiloxane based nano-coating to be coated over Cu-U bends, brazing joints, interconnecting Cu-pipe, GI sheet and Al fins. The coating shall have temperature resistance from -25 degrees to 450 degrees after full cure with salt spray resistance of up-to 3000 hrs. as per ASTM B-117 along with excellent abrasion resistance, chemical/UV resistance, and heat dissipation properties. Coating shall be pigmented as recommended for better distinguishing between coated and un-coated areas. The polymer shall be obtained by mixing base and hardener and applied by air assisted spray with thickness of coating should be 15-20 micron, coated prior to delivery at site and all copper ref piping shall also be epoxy coated post installation at site. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Pipe Size Thickness of CSE |  |  |  |  | 0 | 0
| (O.D.) Insulation |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | 34.9 mm 19 mm | Rmt |  |  |  | 0 | 0
b. | 28.6 mm 19 mm | Rmt |  |  |  | 0 | 0
c. | 25.4 mm 19 mm | Rmt |  |  |  | 0 | 0
d. | 22.2 mm 19 mm | Rmt |  |  |  | 0 | 0
e. | 19.1 mm 13 mm | Rmt |  |  |  | 0 | 0
f. | 15.9 mm 13 mm | Rmt |  |  |  | 0 | 0
g. | 12.7 mm 13 mm | Rmt | 10 |  |  | 0 | 0
h | 9.5 mm 13 mm | Rmt |  |  |  | 0 | 0
i | 6.4 mm 13 mm | Rmt | 10 |  |  | 0 | 0
[6 empty] | 0 | 0
2.2 | FITTINGS |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing & Commissioning of following imported copper fittings to be provided in refrigerant pipe line. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | Refnet Joints (Y- Joints) | Nos |  |  |  | 0 | 0
b. | Refnet Headers | Nos |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.3 | CONDENSATE DRAIN PIPING -cPVC |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Commissioning of cPVC pipes cut to required lengths and installed for condensate drain. Quoted price shall be inclusive of supply and fixing in position the necessary fittings like elbows, tees reducers etc., and supporting arrangement in accordance with the approved shop drawings and specifications. Pipes shall be insulated with 9mm thick closed cell elastomeric insulation with aluminium foil & class 'O' fire retardant properties in tubing form. Pipes shall be of following sizes : |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | 40mm dia | RM |  |  |  | 0 | 0
b. | 32mm dia | RM | 5 |  |  | 0 | 0
c. | 25mm dia | RM | 10 |  |  | 0 | 0
[6 empty] | 0 | 0
| TOTAL ITEM NO. 2 (PIPING) |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
3 | ELECTRICAL WORKS |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
3.1 | PANELS-For VRV System | Shall be covered in main electrical package |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Commissioning of the following cubical type panels made out of 14 gauge CRCA structure, base channel, complete with, moulded case circuit breakers, meters, indicating lamps, current transformer etc. Complete in all respects, insulated bus bars with heat shrinkable PVC sleeve in suitable bus chambers, interconnection, small wiring, name plate, danger plate, earth bus etc. & comprising of compartments with hinged door for each feeder & its accessories, cable alley with hinged doors, bus chamber with bolted door etc. The panel being of dust & vermin proof construction with rubber gasket attractively powder coating etc. The panel shall be free standing type / wall mounted type having IP-65 Protection suitable for outdoor installation as per relevant drawing and comprising with the following: |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Notes : |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 1. All MCCBs shall be with operating handle. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 2. CTs burden shall be 15VA & accuracy class 1.0 |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 3. CTs shall be cast resin type . |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 4. All MCCBs shall be with thermal magnetic release. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 5. All indication lights shall be LED type. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 6. All meter shall be digital type. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 7. The outgoing starter feeders for pumps, AHUS |  |  |  |  | 0 | 0
| & ventilation fans shall be provided |  |  |  |  | 0 | 0
| with push buttons & indicating lamps for |  |  |  |  | 0 | 0
| status indication. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 8. Proper isolation switches to be |  |  |  |  | 0 | 0
| provided near air handling units and |  |  |  |  | 0 | 0
| ventilation fans in weather proof enclosure. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 9. Bimetal overload relay for all the starters shall have built-in single phasing prevention feature. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 10. Electrical interlocking wiring shall be provided as per system requirement. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 11. Power cabling/wiring with necessary earthing from source to each panel and each exhaust fan shall be provided by other agencies. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Note : |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
i. | Incoming power supply shall be provided by main |  |  |  |  | 0 | 0
| electrical contractor/electrical consultant at each VRV |  |  |  |  | 0 | 0
| outdoor unit along with a TPN MCCB and earthing. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
3.2 | CONTROL & TRANSMISSION WIRING |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, laying, affecting connections and Testing of the following sizes of control cum transmission wiring to be laid in MS conduits between indoor units and outdoor units. |  |  |  |  | 0 | 0
| 2C x1.5 Sqmm copper wiring | Rmt | 10 |  |  | 0 | 0
[6 empty] | 0 | 0
3.3 | CONTROLLER WIRING |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, laying, affecting connections and Testing of the following sizes of control cum transmission wiring to be laid in MS conduits between indoor units and their wired remotes. |  |  |  |  | 0 | 0
| 2C x1.5 Sqmm copper wiring | Rmt | 0 |  |  | 0 | 0
[6 empty] | 0 | 0
TOTAL (AIR DISTRIBUTION) Rs. | TOTAL ITEM NO. 3 (ELECTRICAL) |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
SECTION 'D' - HYDROGEN EXHAUST FOR BATTERY ROOM | [5 empty] | 0 | 0
[6 empty] | 0 | 0
1 | INLINE FANS - For Hydogen Exhaust |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Commissioning of circular inline fans for exhaust complete with sheet metal casing, direct driven centrifugal fan constructed out of GSS, class "B" insulated motor with proper protection and inspection door. Fan shall be suitable for operation on 415 ±10% volts, 50Hz, 3 phase AC power supply. Flanges to be provided on both sides to facilitate duct connections. Fan shall be provided with factory fitted speed regulation arrangement. Fan shall be Explosion Proof Type. Fan shall be installed as shown in the drawings and will be of following characteristics : |  |  |  |  | 0 | 0
| Quoted price shall be inclusive of gravity louvers. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Fan Capacity S.P Area to |  |  |  |  | 0 | 0
| No. (Cfm) (mmWG) to be exhausted |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| IF-1 250 15-16 Battery Room | No | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
2 | HYDROGEN SENSORS |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Fixing and Testing of H2 Sensors. Sensors should be capable to give command directly to Inline fan panel after increasing of H2 level beyond certain specified levels. Quoted price shal be inclusive of Power cabling and control cabling as required between sensor & panels etc. Sensors should be able to automatically switch ON/OFF the Fans after increasing/control of H2 level beyond certain specified levels respectively. Price shall also be inclusive of all accessories required to make installation complete whether specified or not. H2 sensors shall be capable for BMS Integration as well. | No | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
3 | Panels - Hydrogen Exhaust |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Commissioning of the following cubical type panels made out of 14 guage CRCA structure, base channel, complete with, moulded case circuit breakers, meters, indicating lamps, current transformer etc. Complete in all respects, insulated bus bars with heat shrinkable PVC sleeve in suitable bus chambers, interconnection, small wiring, name plate, danger plate, earth bus etc. & comprising of compartments with hinged door for each feeder & its accessories, cable alley with hinged doors, bus chamber with bolted door etc. The panel being of dust & vermin proof construction with rubber gasket attractively powder coating etc. The panel shall be free standing type / wall mounted type as per relavant drawing and comprising with the following: |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Notes : |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 1. All MCCBs shall be with operating handle. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 2. CTs burden shall be 15VA & accuracy class 1.0 |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 3. CTs shall be cast resin type . |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 4. All MCCBs shall be with thermal magnetic |  |  |  |  | 0 | 0
| release. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 5. All indication lights shall be LED type. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 6. All meter shall be digital type. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 7. The outgoing starter feeders for pumps,AHUS |  |  |  |  | 0 | 0
| & ventilation fans shall be provided |  |  |  |  | 0 | 0
| with push buttons & indicating lamps for |  |  |  |  | 0 | 0
| status indication. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 8. Proper isolation switches to be |  |  |  |  | 0 | 0
| provided near air handling units and |  |  |  |  | 0 | 0
| ventilation fans in weather proof enclosure. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 9. Bimetal overload relay for all the |  |  |  |  | 0 | 0
| starters shall have built-in single |  |  |  |  | 0 | 0
| phasing prevention feature. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 10. Electrical interlocking wiring shall be |  |  |  |  | 0 | 0
| provided as per system requirement. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 11. Power cabling/wiring with necessary |  |  |  |  | 0 | 0
| earthing from source to each panel |  |  |  |  | 0 | 0
| and each exhaust fan shall be |  |  |  |  | 0 | 0
| provided by other agencies. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 12. All HVAC equipment shall be compatible with |  |  |  |  | 0 | 0
| BMS and necessary provisions to be made |  |  |  |  | 0 | 0
| in each panel. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
3.1 | Explosion Proof Fan Panel-1 (Location : Near Fan) | No | 1 |  |  | 0 | 0
| For Battery Room - 90W |  |  |  |  | 0 | 0
| 1x250Cfm Fan |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 10 Amps ,TP MCB -- 1set |  |  |  |  | 0 | 0
| (0-500) V digital Voltmeter with built in Selector |  |  |  |  | 0 | 0
| switch -- 1set |  |  |  |  | 0 | 0
| Digital Ammeter with built in selector |  |  |  |  | 0 | 0
| switch- 1set |  |  |  |  | 0 | 0
| Current Transformers - 1set |  |  |  |  | 0 | 0
| LED type RYB phase indication lights- 1set |  |  |  |  | 0 | 0
| LED type ON & OFF indication lights -- 1set |  |  |  |  | 0 | 0
| START-STOP Push Buttons -- 1set |  |  |  |  | 0 | 0
| 90 Watt DOL starter with built-in single phasing |  |  |  |  | 0 | 0
| preventer & overload relay -- 1 set |  |  |  |  | 0 | 0
| Auto-Manual type selector switch |  |  |  |  | 0 | 0
| to facilitate auto start of Fans |  |  |  |  | 0 | 0
| after restoration of power -- 01 set. |  |  |  |  | 0 | 0
| Timer for Scheduled On/Off-- 01 set. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Contactors, Potential Free Contacts, Control wiring and |  |  |  |  | 0 | 0
| safety circuit as required with start-stop push buttons |  |  |  |  | 0 | 0
| stay put or lockable type -1 set. |  |  |  |  | 0 | 0
| (Panel to be integrated with Hydrogen Sensor for ON/Off operation). |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
4 | CABLING |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
4.1 | Supply, laying, affecting connections and Testing of the following sizes of 1.1 KV armoured PVC insulated copper/ aluminium conductor cables. Cables shall be inclusive of all clamps, saddles, screws, cable identification tags, cable terminal joints including terminal lugs, insulating tapes, affecting terminal connections to the equipment as per the specifications and as required. Quoted price shall be inclusive of perforated duly painted 2mm thick MS trays and 8 SWG copper earth wire for AHUs. |  |  |  |  | 0 | 0
| All cables shall be FRLS type. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | 3 C x 2.5 Sqmm cable (Copper) | RM | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
TOTAL (AIR DISTRIBUTION) Rs. | TOTAL - HYDROGEN EXHAUST |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
SECTION 'H' - AIR PURIFICATION SYSTEM | [5 empty] | 0 | 0
[6 empty] | 0 | 0
1 | INDOOR AIR PURIFYING IONISERS |  |  |  |  | 0 | 0
| (REME Cell/Bi Polar Plasma Ionnisers) |  |  |  |  | 0 | 0
| Air purification for ceiling suspended Ductable indoor units and AHU The air purification system should be suitable to reduce harmful pollutants like particulate matter (PMx), PM 2.5, allergens, pollen, smoke, bacteria, pathogens etc. based on below principle technology viz;Impingement, Polarisation and Agglomeration as a passive air It should be a slim structured unit specifically designed for integration in Return Air path of ceiling suspended indoor units, to centrally capture. It should be equivalent to Merv-14 or Higher efficiency for AHU and Ductable* Units with low pressure drop. It should have 3x working principles and it should be aluminium based or powder coated steel casing and should be self-contained. It should be a US patented technology with UL certified components. The units shall meet ANSI/ASHRAE 52.2 standards and have valid test report to verify filtration efficiency. The Basic Media of Electric Filter shall Carry Class 2 Fire Rating Listing by UL.The CAC filter/Electrostatic percipitator (ESP), which have Metal based collection plate shall not be accepted. The Supplier shall carry UL2998 certification or at least Acknowledgement letter from UL2998 for testing against Zero Ozone Emission. The system shall be integrated with the existing pre-section filter area of AHU. The test report for pressure drop need to be submitted for passive air purification and the same shall be demonstrated at site. |  |  |  |  | 0 | 0
| Electronic filters should consist of an Internet of Things (IoT) based Smart Filtration option employing a 3-Tier Architecture. This architecture would serve to identify pressure drops across the filter, indicating when a replacement is necessary due to clogged filters. Furthermore, it should gauge levels of filter blockage, enabling scheduled preventive maintenance to ensure sustainability. To facilitate user interaction, a well-designed UI/UX experience in the form of a dashboard is essential, complete with appropriate color-coding. Additionally, the system should generate alerts and notifications via text messages or emails to signal instances of filter clogging or the need for filter replacement. To enhance compatibility, the system must support various communication protocols, including options such as WiFi, Bluetooth Low Energy, Modbus RS485, or LoRaWAN. |  |  |  |  | 0 | 0
| The Active Air Purification system should consist of Supply, Installation, Testing and commissioning of Bipolar Ionisation System. The Bipolar Ionisation System must be a combination of Tube Based Model and Needle Point Model (Needle Point should have Nitinol (nickel titanium) Needles) and Carbon Fibre Brush Model, System should produce positive and negative ions for creating a Bio Climate rich in ions and hence neutralising harmful pollutants including pathogens, Volatile Organic Compounds and Particulate Matter. The Carbon Brush self-balancing ionizer should be installed at the fan inlet of fan coil units, VRF cassettes, ductless splits , AHU and Ductable HVAC System. |  |  |  |  | 0 | 0
| The Carbon Brush and Self Cleaning nickel titanium based Needle Point Bipolar Ionizer must be UL-2998, UL 2043, UL 1995, ISO16000 , CSA C22.2# 187, and CARB. |  |  |  |  | 0 | 0
| Manufacturers shall provide Test report from Internationally/Nationally recognized Lab for proven efficacy on below pathogens with minimum kill rates for the following pathogens given the allotted time and in a space condition: a) SARS-CoV-2 (COVID-19) Human Strain b) MS2 Bacteriophage (Surrogates COVID-19) c) Omicron Variant of SARS-CoV-2 d) H1N1 e) Total Bacterial Count Reduction rate of more than 90% from NABL Accredited Lab f) Yeas & Mold/Total fungal count Reduction rate of more than 90% from NABL Accredited Lab |  |  |  |  | 0 | 0
| *Subject to Available Static as per OEM Technical Data Sheet. |  |  |  |  | 0 | 0
| Ionizers shal be suitable for following Equipment |  |  |  |  | 0 | 0
| Total Nos. of ionisers shall be as per air quantity distributed in individual duct drawn from main plenum/ AHUs in approved shop drawing. |  |  |  |  | 0 | 0
a. | 26,400 CFM FM AHU | Set |  |  |  | 0 | 0
b. | 10,000 CFM FM AHU | Set | 1 |  |  | 0 | 0
c. | 2500 CFM CS AHU | Set |  |  |  | 0 | 0
d. | 1200 CFM FAN COIL UNIT | Set |  |  |  | 0 | 0
[6 empty] | 0 | 0
2 | INDOOR AIR QUALITY MONITOR PORTABLE TYPE |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing & commissioning of IAQ Monitor to measure the levels of PM 2.5, VOCs, CO2, Temperature, Humidity on a real time basis. The IAQ Monitor shall be RS485 enabled and should be capable of getting connected with Wi-Fi. Units should have dedicated data browse i.e. sim card etc. The Monitor should be capable of sending the indoor air quality information on display Screen/Mobile/Workstation as per Client's requirement. The Monitor should indicate the quality of air through changing the colours as per the NAAQS standards and should meet the WELL building standards. Quoted price shall be inclusive of all necessary arrangement as required to make the unit proper functional. (LED Screen not included.) | Nos. | 1 |  |  | 0 | 0
| Supply, Installation, Testing & commissioning of IAQ LED Display Screen | Nos. | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
| TOTAL |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
SECTION 'I' : CHW BASED CS FCU FOR LIFT LOBBY | [5 empty] | 0 | 0
[6 empty] | 0 | 0
1.0 | EQUIPMENT |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
1.1 | FAN COIL UNIT (AHUs) |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
1.1.1 | Ceiling Suspended type AHUs - With Thermal Break Profile and Mixing Chamber |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and commissioning of Chilled water Fan coil unit of double skin construction with compact cooling coil, multispeed fan motor, the blower shall be dynamicaly balanced and designed for silent operation, the filters shall be washable synthetic media type arranged for convenient cleaning and replacement, drain pan with pump drawing of following capacities. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | CHILLED WATER FAN COIL UNITS 3.0 TR (1200 CFM) | No |  |  |  | 0 | 0
[6 empty] | 0 | 0
| TOTAL ITEM NO. 1 (EQUIPMENT) |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.0 | PIPING AND VALVES |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.1 | CHILLED WATER PIPING |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Commissioning of MS heavy class (Class "C') pipes cut to requird lengths and installed with all welded joints. Quoted price shall be inclusive of supply and fixing in position the necessary fittings like elbows, tees reducers, sockets etc., and hanging arrangement and floor supports as required, rigid PUF saddles, washers and check nuts etc in accordance with the approved shop drawings and specifications. All sleeves in Fire wall/slab shall be sealed using fireproof sealant. Pipes shall be of following sizes : |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| For Pipe sizes of 80mm dia & above complete "C" channel support shall be provided. For floor supports, supports shall be complete with pipes of adequate size with base plate & vibration isolation pads and "C" channel. All pipe supports channels, fastner etc. to be selected as per support depth & loading as per structural consultant recommendations. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a | 50mm dia | Rmt |  |  |  | 0 | 0
b | 40mm dia | Rmt |  |  |  | 0 | 0
c | 32mm dia | Rmt |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.2 | CONDENSATE DRAIN PIPING -GI |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Commissioning of GI medium class (Class 'B') pipes cut to requird lengths and installed with all screwed joints for condensate drain. Quoted price shall be inclusive of supply and fixing in position the necessary fittings like elbows, tees reducers etc., and supporting arrangement in accordance with the approved shop drawings and specifications. Pipes shall be insulated with 9mm thick closed cell elastomeric insulation with class 'O' fire retardant properties in tubing form. Pipes shall be of following sizes : |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | 25 mm dia | RM |  |  |  | 0 | 0
b. | 32 mm dia | RM |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.3 | CONDENSATE DRAIN PIPING -cPVC |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Commissioning of cPVC pipes cut to required lengths and installed for condensate drain. Quoted price shall be inclusive of supply and fixing in position the necessary fittings like elbows, tees reducers etc., and supporting arrangement in accordance with the approved shop drawings and specifications. Pipes shall be insulated with 9mm thick closed cell elastomeric insulation with class 'O' fire retardant properties in tubing form. Pipes shall be of following sizes : |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | 25 mm dia | RM | 10 |  |  | 0 | 0
b. | 32 mm dia | RM |  |  |  | 0 | 0
c. | 40 mm dia | RM |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.4 | BUTTERFLY VALVES |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Providing and fixing in position the following wafer type Butterfly Valves complete with SS-410 disc, companion flanges, nuts, bolts, gaskets etc. as required. Butterfly valves shall confirm to PN -16 rating as per specifications. Quoted price shall be inclusive of insulation for valves associated with chilled water circuit as per the specifications. The valves shall be following sizes. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | 32 mm dia | No | 1 |  |  | 0 | 0
b. | 40mm dia | No |  |  |  | 0 | 0
c. | 50mm dia | No |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.5 | BALANCING VALVES |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Commissioning of following Balancing Valves in accordance with the approved shop drawings and specifications. Balancing valves shall conform to PN-16 rating as per the specifications. Quoted price shall be inclusive of insulation as per the specifications. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | 65mm dia | No |  |  |  | 0 | 0
b. | 50mm dia | No |  |  |  | 0 | 0
c. | 40mm dia | No |  |  |  | 0 | 0
d. | 32mm dia | No | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
2.6 | Chilled Water Valve Kit |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Commissioning of Fully Insulated FCU kit comprising of 2 No. Ball valve one with Y-strainer and other with strainer, drain cock, by pass arrangement, On-Off type 2 way motorised valves suitable for heating-cooling thermostat, conduiting, copper wiring etc. for Cassette units/FCUs. Valve should be suitable for operation on 220±6 % volts, 50 Hz,1phase AC power supply. the valve kit shall be PN25 rating |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | 32mm dia valves for 2.5 TR - 3.0 TR. fan Coil Unit | No |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.7 | GATE VALVES |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Commissioning of following Gate Valves in accordance with the approved shop drawings and specifications. Quoted price shall be inclusive of insulation as per the specifications. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | 32mm dia | Nos | 0 |  |  | 0 | 0
b. | 25mm dia | Nos |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.8 | THERMOMETERS |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Commissioning of 100mm dia dial type thermometers as per the specifications. | Nos | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
2.9 | PRESSURE GAUGES |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Commissioning of 100mm dia dial type thermometers as per the specifications. | Nos | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
2.1 | BTU METERS |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Commissioning of Ultrasonic BTU Meters of following sizes. Quoted price shall be complete with control cabling, flanges, gaskets and any other accessories required to complete the system requirement. BTU Meters shall be BMS compatible with Modbus RS 485 protocol. |  |  |  |  | 0 | 0
|  | Nos | 1 |  |  | 0 | 0
a | 40mm dia | Nos |  |  |  | 0 | 0
b | 32mm dia |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
2.11 | FIRE STOPPING FIRE SEALING |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Sealing and fire stopping of vertical duct / pipe risers at each floor level with foam type Sealing System after installation of duct / pipe.Foam after solidifying shall have 2 hour fire rating. | Sqm | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
2.12 | BMS INTERFACE |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Necessary sockets and nipples with shut off valves for mounting sensors/transmitters on pipe line to interface the BMS system. | Lot |  |  |  | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
| TOTAL ITEM NO. 2 (PIPING & VALVES) |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
3 | CHW PIPE INSULATION |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
3.1 | Using Closed Cell Elastomeric Insulation with Class 'O' |  |  |  |  | 0 | 0
| fire retardant properties |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply and Application of 25mm/32mm thick closed cell elastomeric insulation in tubing form /flat sections for chilled water piping as per the specifications. Quoted price shall be inclusive of adhesive as per specifications. Joints shall be sealed with adhesive forming proper bonding. Quoted price shall be inclusive of 24 G aluminium cladding for chilled water piping. |  |  |  |  | 0 | 0
| Adhesive should be Fire Retardant, LEED compliant and Low VOC. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | 65mm dia (25mm thick) | RM |  |  |  | 0 | 0
b. | 50mm dia (25mm thick) | RM |  |  |  | 0 | 0
c. | 40mm dia (25mm thick) | RM |  |  |  | 0 | 0
d. | 32mm dia (25mm thick) | RM | 10 |  |  | 0 | 0
[6 empty] | 0 | 0
| TOTAL ITEM NO. 3 (INSULATION) |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
4.0 | ELECTRICAL WORKS |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
4.1 | AHU Panels |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, Installation, Testing and Commissioning of the following cubical type panels made out of 14 guage CRCA structure, base channel, complete with, moulded case circuit breakers, meters, indicating lamps, current transformer etc. Complete in all respects, insulated bus bars with heat shrinkable PVC sleeve in suitable bus chambers, interconnection, small wiring, name plate, danger plate, earth bus etc. & comprising of compartments with hinged door for each feeder & its accessories, cable alley with hinged doors, bus chamber with bolted door etc. The panel being of dust & vermin proof construction with rubber gasket attractively powder coating etc. The panel shall be free standing type / wall mounted type as per relavant drawing and comprising with the following : |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Notes : |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 1. All MCCBs shall be with operating handle. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 2. CTs burden shall be 15VA & accuracy class 1.0 |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 3. CTs shall be cast resin type . |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 4. All MCCBs shall be with thermal magnetic |  |  |  |  | 0 | 0
| release. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 5. All indication lights shall be LED type. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 6. All meter shall be digital type. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 7. The outgoing starter feeders for pumps,AHUS |  |  |  |  | 0 | 0
| & ventilation fans shall be provided |  |  |  |  | 0 | 0
| with push buttons & indicating lamps for |  |  |  |  | 0 | 0
| status indication. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 8. Proper isolation switches to be |  |  |  |  | 0 | 0
| provided near AHUs units and |  |  |  |  | 0 | 0
| ventilation fans in weather proof enclosure. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 9. Bimetal overload relay for all the |  |  |  |  | 0 | 0
| starters shall have built-in single |  |  |  |  | 0 | 0
| phasing prevention feature. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 10. Electrical interlocking wiring shall be |  |  |  |  | 0 | 0
| provided as per system requirement. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 11. Power cabling/wiring with necessary |  |  |  |  | 0 | 0
| earthing from source to each panel |  |  |  |  | 0 | 0
| and each exhaust fan shall be |  |  |  |  | 0 | 0
| provided by other agencies. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| 12. Necessary provisions shall be made in the panels |  |  |  |  | 0 | 0
| by means of providing necessary relays etc to |  |  |  |  | 0 | 0
| facilitate Building Automation System (BAS) |  |  |  |  | 0 | 0
| integration. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
4.1.1 | AHP-1 (Location: Near AHU) |  |  |  |  | 0 | 0
| For AHUs- 1x5.5/7.5KW | Nos | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
| 25 Amps ,TP MCCB -- 1set |  |  |  |  | 0 | 0
| (0-500) V digital Voltmeter with built in Selector |  |  |  |  | 0 | 0
| switch -- 1set |  |  |  |  | 0 | 0
| Digital Ammeter with built in selector |  |  |  |  | 0 | 0
| switch- 1set |  |  |  |  | 0 | 0
| Current Transformers - 1set |  |  |  |  | 0 | 0
| LED type RYB phase indication lights- 1set |  |  |  |  | 0 | 0
| LED type ON & OFF indication lights -- 1set |  |  |  |  | 0 | 0
| 3HP/2HP DOL starter with built-in single phasing |  |  |  |  | 0 | 0
| preventor & overload relay -- 1set |  |  |  |  | 0 | 0
| START-STOP Push Buttons -- 1 set |  |  |  |  | 0 | 0
| Auto-Manual type selector switch |  |  |  |  | 0 | 0
| to facilitate auto start of AHUs -- 1set |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Contactors, Potential Free Contacts, Control wiring and |  |  |  |  | 0 | 0
| safety circuit as required with start-stop push buttons |  |  |  |  | 0 | 0
| stay put or lockable type -1set |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
4.2 | CABLING |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
| Supply, laying, affecting connections and Testing of the following sizes of 1.1KV armoured PVC insulated copper/aluminium conductor cables. Cables shall be inclusive of all clamps, saddles, screws, cable identification tags, cable terminal joints including terminal lugs, insulating tapes, affecting terminal connections to the equipment as per the specifications and as required. Quoted price shall be inclusive of perforated duly painted 2mm thick MS trays and 8 SWG copper earth wire for AHUs. |  |  |  |  | 0 | 0
| All cables shall be FRLS type. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | 3 C x 6 Sqmm cable (Copper) | RM |  |  |  | 0 | 0
b. | 3 C x 4 Sqmm cable (Copper) | RM |  |  |  | 0 | 0
c. | 3 C x 2.5 Sqmm cable (Copper) | RM | 5 |  |  | 0 | 0
d. | 3 C x 2.5 Sqmm cable( Copper Control cabling) | RM |  |  |  | 0 | 0
e. | 3 C x 1.5 Sqmm cable(Copper Control cabling) | RM |  |  |  | 0 | 0
f. | 4 C x 1.5 Sqmm cable( Copper Control cabling) | RM | 5 |  |  | 0 | 0
[6 empty] | 0 | 0
4.3 | Supply and fixing of 1.1 KV grade rubber mat 914.4 mm wide 6mm thick to withstand 1.1 KV dielectric strength in front of each panel. | RM | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
4.4 | Supply, Installation & Testing of TPN isolator in weather proof enclosure near AHUs & Pumps. | No |  |  |  | 0 | 0
[6 empty] | 0 | 0
| TOTAL ITEM NO. 4 (ELECTRICAL) |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
SECTION 'J' : DEMAND CONTROL VENTILATION & VFD For AHU & FA FAN | [5 empty] | 0 | 0
[6 empty] | 0 | 0
1 | VARIABLE FREQUENCY DRIVES |  |  |  |  | 0 | 0
| Supply, Installation, Testing and Commissioning of variable frequency drives for following Air Handling Units. Variable frequency drives shall be provided with necessary sensors and transmitters complete with control wiring in all respect as required and as per specifications. VFDs shall have built-in harmonic filters. The drives shall be suitable for the following motor rating. VFDs shall be housed in precoated, vandal proof enclosure with On/Off Push Buttons, Phase indication lights, A/M Switch and with adequate provisions for ventilation using a fan. The VFDs shall be able to receive the signals from multiple/combination of duct static pressure sensors/Temp. sensors and to ramp the speed of the motor.VFDs shall be suitable to take feed back and connectivity from all the DPS as mentioned below against each motor rating to facilitate averaging activity by VFD. Quoted price shall be inclusive of return air temperature sensor and necessary electrical switches including change over switch & copper cabling for integration with the AHU panel. VFDs shall be installed within Electrical panels as described under Section 'Electrical Works'. Overall protection of VFDs with Panels shall be IP-54. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | 0.5 KW for Fresh air fan | Nos. |  |  |  | 0 | 0
b. | Up To 7.5 KW for F/M AHU | Nos. | 1 |  |  | 0 | 0
c. | 11.0 KW for F/M AHU | Nos. |  |  |  | 0 | 0
d. | 15.0 KW for F/M AHU | Nos. |  |  |  | 0 | 0
[6 empty] | 0 | 0
2 | VAQ station |  |  |  |  | 0 | 0
| VAQ station shall be dynamically calibrated and is capable of receiving demand signal from CO2 sensors or BMS.Complete with programmable, DDC Advanced Application Controller that communicates on direct digital control using point 2 point analog controls with CO2 sensors, differential pressure sensor & step down transformer of 24V. |  |  |  |  | 0 | 0
| 1059 CFM | Nos. |  |  |  | 0 | 0
| 2119 CFM | Nos. | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
3 | CO2 SENSOR |  |  |  |  | 0 | 0
| Providing & fixing of CO2 Sensor with controllers on the return air side of the ahu / CSU to operate fresh air damper (To Measure the CO2 level of the air conditioned area) | Nos. | 1 |  |  | 0 | 0
| TOTAL ITEM NO. 5 (Demand control ventilation & VFD) |  |  |  | Rs. | 0 | 0

## IBMS
PROJECT: EY CORAL 8TH FLOOR
DATE: 01.07.2024
S.NO | ITEM DESCRIPTION | UNIT | 8TH FLOOR | SUPPLY RATE | INSTALLATION RATE | SUPPLY AMOUNT | INSTALLATION AMOUNT
1 | TOTAL PRICE OF BUILDING AUTOMATION SYSTEM |  |  |  |  | 0 | 0
2 | Dismantling , packing, keeping in store , re installation , testing and commissioning of all IBMS components. |  |  |  |  | 0
| GRAND TOTAL |  |  |  |  | 0 | 0
1 | BUILDING AUTOMATION SYSTEM (BAS)
| Supply, Installation, Testing & Commissioning of Building Management System (BMS). BMS shall be complete as per point schedule suitable to monitor, operate & control the total air conditioning system as well as other systems from a central location Computer. The system shall be complete with all accessories including Server Computer, System/ Network Controller, DDC, Graphics Software, sensors, control valves, actuators, network & electronic components, transformers, relays & associated cabling, conduiting, control wiring, Enclosures etc. as required to make the system operative and functional. Any accessories required for messaging (SMS on Phone) and E-Mailing of alarms to be included in BMS. |  |  |  |  | 0 | 0
| BMS Vituralisation - Complete BMS including hardwares & softwares should be capable of virtualization in future without any changes in BMS set Up. 1. BMS application and hardware: a) The proposed BMS system must support DHCP b) The proposed BMS system must support 802.1xx c) The Proposed BMS system must support IPv4 and should be upgradable to IPv6. |  |  |  |  | 0 | 0
1.1 | CENTRAL CONTROL STATION |  |  |  |  | 0 | 0
| Supply, Installation, Testing & Commissioning of Central Control Station consisting of the following accesories of approved make & as per specifications. |  |  |  |  | 0 | 0
a. | PC i7 Intel Processor, 2.93 Ghtz or better, 8GB RAM (Expandable), 512GB SSD, 2GB NVIDIA graphic card & 32" inch TFT colour monitor, laser printer, cordless key board, mouse, Windows 11 operating system, etc. all complete | No. | 1 |  |  | 0 | 0
b | Required UPS for Controllers, Sensors & Computer with minium 30 minutes backup. | Nos | 1 |  |  | 0 | 0
1.2 | CENTRAL GRAPHICS SOFTWARE |  |  |  |  | 0 | 0
| Supply, Developing, Testing and Commissioning of BTL Listed B-BC, B-OWS profile BMS software with unlimited points license c/w Network interface and Hardware and software required for E mail and SMS alerts and UL Listed BACnet/Modbus Supervisory Controller suitable for Required Data Point Summary (considering 30% extra data points). | Set | 0 |  |  | 0 | 0
| Minimum 5 concurrent user License & unlimited users capacity for the proposed BMS software. Defined users shall be able to view the details through Desktop, Mobile or Ipad with auto adjust views based on the type of the device with 2D/ 3D vector graphics. Software shall accept all open protocols such as BACnet, Modbus, Lonworks, web services etc. The Software shall be Capable for integration & inter-operability with 3rd party microprocessor systems of various Building Services such as UPS, AHUs, VRV Units, VAV Boxes, WLD, VESDA, Pre Action, Fire Alarm, temperture Sensor etc. The software shall collect, view, and analyze trend of informations, display of logs etc. |  |  |  |  | 0 | 0
1.3 | THIRD PARTY INTEGRATION |  |  |  |  | 0 | 0
| Supply,Installation,Testing & commissioning of BTL Listed/ UL listed Integration Modules for High Level integartion with following 3rd Party Equipments. The Integrator shall be Capable of Integrating with any of the Industry accepted Protocol including but not restricted to M-BUS/BACnet / MODBUS RTU / Lonworks, provided on either a RS485 / over IP. Integration units to be of same OEM as software & DDC controller. BMS vendor to consider required Integrators as per IO summary and as per actual requirement. | Set | 0 |  |  | 0 | 0
| AHU by Developers - 8 Nos. |  |  |  |  | 0 | 0
| AHU by Client - 1 Nos. |  |  |  |  | 0 | 0
| FCU by Clients - 0No. |  |  |  |  | 0 | 0
| VAV Integrator - 8No. |  |  |  |  | 0 | 0
| Hydrogen Sensor & Exhaust Fan - 0 No |  |  |  |  | 0 | 0
| NOVEC Extract Fans - 1 No. |  |  |  |  | 0 | 0
| VRV Centralized Controller - 0 Nos. |  |  |  |  | 0 | 0
| IAQ Sensors - 2 Nos. |  |  |  |  | 0 | 0
| CO2 Sensors - 4 Nos. |  |  |  |  | 0 | 0
| Fire Dampers - 30 Nos. |  |  |  |  | 0 | 0
| Critical Area T+RH Monitors- 2 Nos. |  |  |  |  | 0 | 0
| UPS- 4 Nos. |  |  |  |  | 0 | 0
| Fire Alarm Repeater Panel - 2 No. |  |  |  |  | 0 | 0
| Rodent Repellent System- 4 Nos. |  |  |  |  | 0 | 0
| WLD-2Nos. |  |  |  |  | 0 | 0
| Energy Meters - 4 Nos. |  |  |  |  | 0 | 0
| NOVEC - 1 No. |  |  |  |  | 0 | 0
| VESDA - 1 No. |  |  |  |  | 0 | 0
| Water Meters - 4 Nos. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
1.4 | CONTROLLERS |  |  |  |  | 0 | 0
| Direct Digital Controllers (DDC), BTL Listed, UL listed with peer to peer communication, BACNET/IP, battery Back up, Enclosed in a vandal proof, lockable, well secured MS powder coated enclosure, as per input / output summary. |  |  |  |  | 0 | 0
| All DDC Controllers with necessary enclosure panels shall be provided with hinged doors with locking facility and back plate. Apart from the controllers, the enclosures shall house the terminal blocks, transformer, internal wiring, load relays and associated equipment. The internal wiring in the enclosure shall be factory wired. The packaging shall be such that complete installation of the field equipment and field wiring can be done prior to the installation of the DDC Controllers. 15% overall spare capacity shall be required for DDC controllers. Dedicated DDC tobe provided for each AHU. The controllers shall be complete with MCBs, relays and all accessories as required. | Lot | 1 |  |  | 0 | 0
| DDC to meet data point summary requirement. |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
1.5 | FIELD DEVICES |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a. | Supply, Installation, Testing and Commissioning of following approved make field devices as per specifications. |  |  |  |  | 0 | 0
b. | Outside Air Temperature & RH sensor (combined) | Nos. | 0 |  |  | 0 | 0
c. | Air Differential pressure switches across the fans for monitoring fan status | Nos. | 1 |  |  | 0 | 0
d. | Duct type temperature sensor for AHUs. | Nos. | 1 |  |  | 0 | 0
e. | Wall mount Temp + RH sensor | Nos. | 1 |  |  | 0 | 0
f. | Room Temperature + RH Sensors with display outside room for Hub Room | Nos. | 1 |  |  | 0 | 0
g. | Room Temperature & RH sensors with display. | Nos. | 0 |  |  | 0 | 0
h. | Immersion type temperature sensors for measuring chilled & hot water supply & return temperature with SS pocket (Range 32 - 140 deg. F). | Nos. | 1 |  |  | 0 | 0
i. | CO2 sensor with Modbus RS-485 | Nos | 1 |  |  | 0 | 0
j. | PM2.5 + PM10 sensor with Modbus RS-485 | Nos | 1 |  |  | 0 | 0
k. | Ambient CO2 sensor | No | 1 |  |  | 0 | 0
l. | Flow Sensor to measure intake air flow | Nos | 1 |  |  | 0 | 0
m. | Duct mount Temp + RH sensor | Nos | 1 |  |  | 0 | 0
n. | Differential Pressure Switch -Air | Nos | 1 |  |  | 0 | 0
[6 empty] | 0 | 0
1.6 | WIRING AND CONDUITS |  |  |  |  | 0 | 0
1.6.1 | Supply, Laying, Testing & Commissioning of following Signal & communication cable as per the specifications : |  |  |  |  | 0 | 0
a | CAT 6A FRLS Cable for Communication | RM | 650 |  |  | 0 | 0
b | 4 Cr x 1 Sq.mm. FRLS Shielded. Cable for Field Devices | RM | 650 |  |  | 0 | 0
c | 2 Cr x 1 Sq.mm FRLS Shielded Cable for Field Devices | RM | 300 |  |  | 0 | 0
d | 3 Cr x 1.5 Sq.mm FRLS Cable with Plug Top for DDC Supply from UPS Socket | RM | 650 |  |  | 0 | 0
[6 empty] | 0 | 0
1.6.2 | Supply, installation & testing of MS conduits in 16 gauge thickness of the following sizes including all accessories. |  |  |  |  | 0 | 0
a | 25 mm | RM | 500 |  |  | 0 | 0
b | 20mm Flexible conduit | RM | 200 |  |  | 0 | 0
[6 empty] | 0 | 0
1.6.3 | Supply, Installation & Testing of Perforated Cable tray of width upto 300mm - thickness of metal sheet will be 1.6mm with cover of 24SWG as specified with counter sunk type screws & all accessories. The dimension of the same shall be as follows : |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
a | 100mmX 50MM | RM | 100 |  |  | 0 | 0
b | 150mmX 50MM | RM | 70 |  |  | 0 | 0
c | 300mmX 50MM | RM | 20 |  |  | 0 | 0
[6 empty] | 0 | 0
1.7 | Router |  |  |  |  | 0 | 0
| SITC of Permanent Router - 16 Port (Network Switch & Hub) for BMS controller devices. Network Switch shall be layer-2 10G managed network switch having support for protocols such as ARP, DHCP, RSTP etc, & provide cybersecurity features to attain network security & reliability, having upto 2 SFP port for fibre connectivity with all necessary accessories such as network rack, patch panels, patch chords etc. as per requirement. | Set | 1 |  |  | 0 | 0
1.7.1 | Core Switch Layer-3 | Set | 1 |  |  | 0 | 0
1.7.1 | Core Switch Layer-3
|  |  |  | Rs. |  | 0 | 0
TOTAL - BMS System
Note:
BMS Quantityt taken as per assumption final quantiy & cost as per Final inspection by contractor.
Quantity will is collaborative of 8th & 9th floor