## Firecurtain BOQ - 4 Hr
ITEM NO. | ITEM DESCRIPTION | UNIT |  | QTY. |  |  |  | Rate | Total Amount
|  |  |  | B3 | B2 | B1 | Total
|  |  | HEIGHT @ DRIVEWAY (M) | 3.05 | 3.05 | 3.95
Automatic Fire Curtain
1 | Supply and installation of 240 minutes fire rated Fire Curtain with Galv. MS Head Top Box (200mm x 200mm minimum dimensions), Powder Coated Side Guides (100mm x 53mm minimum dimensions), Adjustment Channels and Bottom Bars with geared motors for power up operation and operated system. Safe fixed into Steel rollers with woven glass fiber fabric, reinforced with stainless steel wire having micronized aluminium polymer coating on each side of the fabric (silver/grey) with its control panel and all installation assemblies & accessories required to complete the installation. The operation shall be suitable for dedicated 230 Volts UPS, 50 Hz AC supply.Complete system tested in accordance with BS EN 1634-1 (for 120 minutes Integrity & tested at 1000°C) to BS 476-22.8 and BS 7346-3. The system is designed and tested to withstand the pressure of 6 bar at the temperature of 1000°C for the period of 120 minutes. The Emergency Retract Switch is needed on both side of the curtain. The curtain should reset automatically when Fire Control Panel is reset. Vendor / Manufacturer to submit valid Test Report for the complete systems and not just for fabric from an independent international accredited laboratory. Accessories includes Top box, Side Guides, Curtains, barrel including motor, dummy end and bottom rail shall be suitable for 2hr fire ratings. The Fire barrier board with insulation BS 476—Part 20, UL 1479, ISO 834, IS 12458 to be provided to fill in the space between the barrel and the slab. Fire FB-250 barrier system, 2hr rating used above fire curtrain wall opening and the material used is -wool board high density firex coated material wool board having thickness of 100mm and 2hr rating. Rated density of 175 kg/m3, over coated with FM approved firex EC 43 coating. Specifically designed for sealing around MEP services running below the slab and above fire curtain. Fire FB-250 system consists of very high density fire and heat resistant material. Wool board coated with water resistance material fixed with firex expanding sealants which transforms into a hard ceramic during a fire to prevent the passage of fire and smoke and the transfer of heat. The rate includes approved make cable running on ceiling / wall / floor etc. complete with accessories like, Junction boxes, Collars, Bends etc,the connection to be taken from the nearest DB. Overall system shall be suitable to withstand 4hr fire rating. The final lengths shall be as per required at site and shall be installed as per approval from EIC.
i | Fire curtain of length 5.35 m | Set |  | 1 | 0 | 0 | 1 | 368500 | 368500
ii | Fire curtain of length 7.5 m | Set |  | 1 | 1 | 1 | 3 | 517000 | 1551000
iii | Fire curtain of length 10.34 m | Set |  | 1 | 0 | 0 | 1 | 606376 | 606376
iv | Fire curtain of length 6.1 m | Set |  | 1 | 0 | 0 | 1 | 375375 | 375375
v | Fire curtain of length 6 m | Set |  | 2 | 3 | 3 | 8 | 375375 | 3003000
vi | Fire curtain of length 4.5 m | Set |  | 1 | 0 | 0 | 1 | 279125 | 279125
vii | Fire curtain of length 6.43 m | Set |  | 1 | 0 | 0 | 1 | 462000 | 462000
| Fire curtain of length 4.27 m | Set |  | 0 | 1 | 1 | 2 | 255063 | 510126
|  |  |  | 8 | 5 | 5 | 18
| Total Amount | [7 empty] | 7155502
8443492.36
Terms & Conditions:
1.Payment Term: 50 % Advance againest PO and 50% before material dispatching
2. Delivery within 4-5weeks from date of release of purchase order approved drawing and advance payment.
3.Scaffolding support to hang the curtain will be provided by the client
4.However any civil work/civil modification location to install the curtain to be done by client
5.Installation is also included in the above price
6.Power supply for installation to be provided by client
7. All goods will remain the property of WindowTechs until paid for in full. We reserve the right to remove any units fitted by ourselves or others until full payment is received.
8.This quote is valid for 60 days only
9. As per Section 16 of the MSME Act, the buyer is liable to pay interest with the monthly rests to the supplier in case of non-payment or delayed payment. The interest is compounded at the rate of 24%.
Regards,
For Window Techs India Pvt.Ltd
Alistair Paiva

## Firecurtain BOQ - 2 Hr
ITEM NO. | ITEM DESCRIPTION | UNIT |  | QTY. |  |  |  | Rate | Total Amount
|  |  |  | B3 | B2 | B1 | Total
|  |  | HEIGHT @ DRIVEWAY (M) | 3.05 | 3.05 | 3.95
Automatic Fire Curtain
1 | Supply and installation of 120 minutes fire rated Fire Curtain with Galv. MS Head Top Box (200mm x 200mm minimum dimensions), Powder Coated Side Guides (100mm x 53mm minimum dimensions), Adjustment Channels and Bottom Bars with geared motors for power up operation and operated system. Safe fixed into Steel rollers with woven glass fiber fabric, reinforced with stainless steel wire having micronized aluminium polymer coating on each side of the fabric (silver/grey) with its control panel and all installation assemblies & accessories required to complete the installation. The operation shall be suitable for dedicated 230 Volts UPS, 50 Hz AC supply.Complete system tested in accordance with BS EN 1634-1 (for 120 minutes Integrity & tested at 1000°C) to BS 476-22.8 and BS 7346-3. The system is designed and tested to withstand the pressure of 6 bar at the temperature of 1000°C for the period of 120 minutes. The Emergency Retract Switch is needed on both side of the curtain. The curtain should reset automatically when Fire Control Panel is reset. Vendor / Manufacturer to submit valid Test Report for the complete systems and not just for fabric from an independent international accredited laboratory. Accessories includes Top box, Side Guides, Curtains, barrel including motor, dummy end and bottom rail shall be suitable for 2hr fire ratings. The Fire barrier board with insulation BS 476—Part 20, UL 1479, ISO 834, IS 12458 to be provided to fill in the space between the barrel and the slab. Fire FB-250 barrier system, 2hr rating used above fire curtrain wall opening and the material used is -wool board high density firex coated material wool board having thickness of 100mm and 2hr rating. Rated density of 175 kg/m3, over coated with FM approved firex EC 43 coating. Specifically designed for sealing around MEP services running below the slab and above fire curtain. Fire FB-250 system consists of very high density fire and heat resistant material. Wool board coated with water resistance material fixed with firex expanding sealants which transforms into a hard ceramic during a fire to prevent the passage of fire and smoke and the transfer of heat. The rate includes approved make cable running on ceiling / wall / floor etc. complete with accessories like, Junction boxes, Collars, Bends etc,the connection to be taken from the nearest DB. Overall system shall be suitable to withstand 2hr fire rating. The final lengths shall be as per required at site and shall be installed as per approval from EIC.
i | Fire curtain of length 5.35 m | Set |  | 1 | 0 | 0 | 1 | 368500 | 368500
ii | Fire curtain of length 7.5 m x 3.95m | Set |  | 1 | 1 | 1 | 3 | 517000 | 1551000
iii | Fire curtain of length 10.34 m | Set |  | 1 | 0 | 0 | 1 | 606376 | 606376
iv | Fire curtain of length 6.1 m | Set |  | 1 | 0 | 0 | 1 | 375375 | 375375
v | Fire curtain of length 6 m x 3.95m | Set |  | 2 | 3 | 3 | 8 | 375375 | 3003000
vi | Fire curtain of length 4.5 m | Set |  | 1 | 0 | 0 | 1 | 279125 | 279125
vii | Fire curtain of length 6.43 m | Set |  | 1 | 0 | 0 | 1 | 462000 | 462000
| Fire curtain of length 4.27 m x 3.95m | Set |  | 0 | 1 | 1 | 2 | 255063 | 510126
|  |  |  | 8 | 5 | 5 | 18
| Total Amount | [7 empty] | 7155502
8443492.36
Terms & Conditions:
1.Payment Term: 50 % Advance againest PO and 50% before material dispatching
2. Delivery within 4-5weeks from date of release of purchase order approved drawing and advance payment.
3.Scaffolding support to hang the curtain will be provided by the client
4.However any civil work/civil modification location to install the curtain to be done by client
5.Installation is also included in the above price
6.Power supply for installation to be provided by client
7. All goods will remain the property of WindowTechs until paid for in full. We reserve the right to remove any units fitted by ourselves or others until full payment is received.
8.This quote is valid for 60 days only
9. As per Section 16 of the MSME Act, the buyer is liable to pay interest with the monthly rests to the supplier in case of non-payment or delayed payment. The interest is compounded at the rate of 24%.
Regards,
For Window Techs India Pvt.Ltd
Alistair Paiva