## Sheet1
|  | Unit | Quantity | Price Per Curtain | Final Amount
5 | " Fire Curtains"UL listed with galvanized MS head box, size( 200X200mm) powder coated, side guides size( 53x100mm) along with adjustment channels & bottom bars with motors for power up operation with standard battery backup & operated system safe fixed into steel rollers with woven glass fibre fabric(Valmiera UK), reinforced with stainless steel wire having micronized aluminium polymer coating on each side of the fabric (silver/grey) with the necessary control panel & all installation assemblies & accessories required to complete the installation. The operation shall be suitable for dedicated 240 Volts UPS, 50 Hz AC supply. Complete system shall be tested in accordance with EN 1634-1 (for 120 minutes Integrity & tested at 1000°C) BS 476-22.8 and BS 7346-3. Quoted rate shall include necessary "Emergency Retract Switch" on both sides of the curtain along with necessary control panel housed within the provided false ceiling depth with suitable supports.Vendor/Manufacturer to submit valid Test Report for the complete systems and not just for fabric from an independent international accredited laboratory. The Test Report of complete system should not be more than 5 years old. Vendor/Supplier should duly submit current dated authorization letter from the manufacturer or principal that he is representing : (NOTE : FIRE CURTAIN SHOULD BE CONCEALED INSIDE THE FALSE CEILING AREA BEFORE FABRICATION OF CURTAIN ASSEMBLY AND ACCESSORIES THE SAME SHOULD BE APPROVED FROM CONSULTANT AND ARCHITECT WITH GAD.) |  | -
| Fire curtain location dependent on RCP layout the quantitys will be considered post the confirmation of fire curtain locations |  | -
| Fire Curtains Sizes |  | -
5.1 | 2.2x 3.0m (Siingle Roll) | No's | 2 | 160000 | 320000
5.2 | 4.2x 3.0m (Siingle Roll) | No's | 2 | 231875 | 463750
SUB TOTAL |  |  |  |  | 783750
GST 18% |  |  |  |  | 141075
FINAL AMOUNT |  |  |  |  | 924825