## Sheet1
III | FIRE CURTAINS | Unit | Qty | Price Per Curtain | Final Amount
1 | Supply, Installation, Testing and Commissioning of automatic fire curtains manufactured in accordance with Latest norms of BS 8524-1:2013 & BS EN 1634-1:2014+A1:2018. Rated upto 240 minutes integrity at 1000 degrees centigrade. The fire curtain assembly briefly comprised a galvanised mild steel headbox containing a steel tube curtain roller mechanism, referenced ‘Motor type 80G’, galvanised mild steel guide rails and a micronized aluminium coated stainless steel reinforced glass cloth curtain fabric and sewn with polymer coated stainless steel thread and conforms to BS476-6:1989 + A1:2009 & BS476-7:1997 (colour –Grey) . System classified to 13501-1:2007+ A1 2009. The motor is a patented 24v DC gravity fail safe tubular motor and is controlled through a panel which includes a battery back-up and a warning siren. The control panel requires a 230/240V UPS AC supply @ 50Hz . In the event of a complete power failure, the curtain will descend under gravity but will retract when power is restored. An emergency retract switch will be sited each side of the curtain to override the programme. The fire curtain system is delivered complete and ready to install, with the head box containing the barrel, motor, curtain and bearings assembled and sealed. Other parts to be assembled on site. All controls are set from the panel provided
All parts will be presented in a powder coated finish to the client’s specification.
A certificate of compliance will be issued following commissioning. authorization letter from the manufacturer or principal that he is representing. The Fire curtain must be compliant to BS 8524-1, BS EN 1634-1.
This shall be integrated with the electrical, BMS, FIre/ Smoke detection system, etc, to ensure complete functionality. The entire system to be designed and executed as per the EN code provisions and tolerances. Contractor to produce design & shop drawings for approval as per Project Consultant / Engineer-in-charge. The work shall be guaranteed for all material & constructional defects. The rate shall include for Design, fabrication, submission & approval of design & shop drawings prior to supply & installation of the Fire Curtains as per design intent drawings. The clear openable size for the Fire curtain as per drawings. Respective Technical Test Certifications and other documents must be submitted to Consultant for approval.
1.5 | Automatice Fire Curtains size to be 3055mm (W) X 2700mm (H) Single Barrel with Egrees Door. | Set | 1 | 145911.2078 | 145911.2078
1.6 | Automatice Fire Curtains size to be 5150mm (W) X 2700mm (H) Single Barrel with Egrees Door. | Set | 1 | 211735.8128 | 211735.8128
1.7 | Automatice Fire Curtains size to be 3080mm (W) X 2700mm (H) Single Barrel with Egrees Door. | Set | 1 | 145911.2078 | 145911.2078
1.8 | Automatice Fire Curtains size to be 5725mm (W) X 2700mm (H) Single Barrel with Egrees Door. | Set | 1 | 228191.964 | 228191.964
1.9 | Automatice Fire Curtains size to be 2305mm (W) X 2700mm (H) Single Barrel with Egrees Door. | Set | 1 | 140425.824 | 140425.824
1.1 | Automatice Fire Curtains size to be 3040mm (W) X 2700mm (H) Single Barrel with Egrees Door. | Set | 1 | 145911.2078 | 145911.2078
1.11 | Automatice Fire Curtains size to be 5270mm (W) X 2700mm (H) Single Barrel with Egrees Door. | Set | 1 | 211735.8128 | 211735.8128
1.12 | Automatice Fire Curtains size to be 3075mm (W) X 2700mm (H) Single Barrel with Egrees Door. | Set | 2 | 145911.2078 | 291822.4155
1.13 | Automatice Fire Curtains size to be 5300mm (W) X 2700mm (H) Single Barrel with Egrees Door. | Set | 2 | 211735.8128 | 423471.6255
1.14 | Automatice Fire Curtains size to be 2710mm (W) X 2700mm (H) Single Barrel with Egrees Door. | Set | 1 | 140425.824 | 140425.824
1.15 | Automatice Fire Curtains size to be 2650mm (W) X 2700mm (H) Single Barrel with Egrees Door. | Set | 1 | 140425.824 | 140425.824
1.16 | Automatice Fire Curtains size to be 3160mm (W) X 2700mm (H) Single Barrel with Egrees Door. | Set | 1 | 145911.2078 | 145911.2078
1.17 | Automatice Fire Curtains size to be 2215mm (W) X 2700mm (H) Single Barrel with Egrees Door. | Set | 1 | 140425.824 | 140425.824
1.18 | Automatice Fire Curtains size to be 5675mm (W) X 2700mm (H) Single Barrel with Egrees Door. | Set | 1 | 228191.964 | 228191.964
1.19 | Automatice Fire Curtains size to be 3145mm (W) X 2700mm (H) Single Barrel with Egrees Door. | Set | 1 | 145911.2078 | 145911.2078
1.2 | Automatice Fire Curtains size to be 3110mm (W) X 2700mm (H) Single Barrel with Egrees Door. | Set | 1 | 145911.2078 | 145911.2078
1.21 | Automatice Fire Curtains size to be 5250mm (W) X 2700mm (H) Single Barrel with Egrees Door. | Set | 1 | 211735.8128 | 211735.8128
1.22 | Automatice Fire Curtains size to be 3105mm (W) X 2700mm (H) Single Barrel with Egrees Door. | Set | 1 | 145911.2078 | 145911.2078
1.23 | Automatice Fire Curtains size to be 5260mm (W) X 2700mm (H) Single Barrel with Egrees Door. | Set | 1 | 211735.8128 | 211735.8128
SUB TOTAL |  |  |  |  | 3601702.9703
GST 18% |  |  |  |  | 648306.5346
FINAL AMOUNT |  |  |  |  | 4250009.5049