## FIRE FIGHTING
Project: | OPTUM, NOIDA
Package: | Supply, Installation, Testing & Commissioning of Fire Fighting System
Sl. No | Description | Approved Make | Unit | Qty | Rate |  | AMOUNT -3rd FLOOR
|  |  |  | 3rd Floor | Supply | Installation | Supply | Installation
C) | SUB HEAD - III- (FIRE CURTAIN)
1 | SITC "Fire Curtains" with galvanized MS head box, size( 200X200/400mm) powder coated, side guides size( 53x100mm) along with adjustment channels & bottom bars with motors for power up operation with standard battery backup & operated system fixed into steel rollers with woven glass fibre (valmiera Glass-UK) fabric, reinforced with stainless steel wire having micronized aluminium polymer coating on each side of the fabric (silver/grey) with the necessary control panel & all installation assemblies & accessories required to complete the installation. The operation shall be suitable for dedicated 240 Volts UPS, 50 Hz AC supply. Complete OFC system shall be tested in accordance with EN 1634-1 (for 120 minutes Integrity & tested at 1000°C) BS 476-22.8 and BS 7346-3. Quoted rate shall include necessary "Emergency Retract Switch" on both sides of the curtain along with necessary OFC control panel (FC01) housed within the provided false ceiling depth with suitable supports.Vendor/Manufacturer to submit valid Test Report for the complete systems and not just for fabric from an independent international accredited laboratory. The Test Report of complete system should not be more than 5 years old. Vendor/Supplier should duly submit current dated authorization letter from the manufacturer or principal that he is representing: | Option -1- Cooper Option -2- Stoibich Option -3- BLE
List of component of Fire Curtains:Top box, Side Guides, Curtains, barrel including motor, dummy end and bottom rail, Control Panel (FC01), Key switch,Override switch(Egress Switch),etc.
1.1 | Single Barrel 850mm X 3000mm |  | Nos | 1 | 150000 | 10000 | 150000 | 10000
1.2 | Single Barrel 1900mmX 3000mm |  | Nos | 1 | 150000 | 10000 | 150000 | 10000
| TOTAL | [5 empty] | 300000 | 20000