## Sheet1
Sl.No | Description | Uom | Qty | Rate | Amount
Supply, Installation, Testing and Commissioning of Fire Curtains with Galvanized MS powder coated head top box of suitable size, Powder coated side guides (100mm x 50mm) and bottom bars with Gravity fail safe DC motors one per roller for curtain up operation with standard battery back-up fixed into 76 / 88 mm steel rollers with FAB690PU fabric must be according to DIN EN 13501-1 and stainless steel reinforced glass fibre with fire-retardant aluminum pigmented polyurethane coating, with its control panel and all installation assemblies & accessories required to complete the installation. The operation shall be suitable for dedicated 230 volts UPS, 50 Hz AC supply. Complete system tested in accordance with en 1634-1 and EN 12101-1 (for minimum 120 minutes integrity & tested at 1,000°C) with CE certificate from European Notified Body. Both test reports EN 1634-1 & EN 12101-1 must be according to the requirement of particular project, if single roller curtain is there then single roller certificates and double roller curtain is there then double roller certificates must be submitted accordingly. The fire curtain must be according to classification of Fire Resistance Performance in Accordance with EN 13501-2 : 2016. The manufacturer’s valid EN certification for oversized firecurtains according to EN 15269-11 covering the sizes of offered fire curtains as per BOQ, should be available. Each fire curtain shall have independent control panel suitable for 230V AC supply, provision to integrate with fire signal and battery backup. The emergency retract switch shall be provided on both sides of curtain. The Fire curtain shall reset automatically when fire control panel is reset. Fabric and all components sourced from the original manufacturer who has valid type test certificate of the fire curtain and third party quality surveillance audit as per above standards including oversize certification according to applicable EN standards. The scope also includes fabrication, supply and installation of closed MS sections corner supports for fixing side channels, design suitable for stability and integrity with two hours fire rating, wherever required for full height of fire curtain, as per approved design, duly finished with powder coating of finish matching to side channels of firecurtains. All the required test / certificates must not be less than 5 Years validity. No mirror certificates allowed. Installation: The fire curtain has fixing options to suit all types of ceiling configurations and can be integrated into either a suspended or a solid ceiling. It remains hidden until required. Upon receiving a signal from the fire detection system or on loss of power with the gravity fail safe system, the curtain automatically unwinds to its operational position.
Fire Curtains System Include: Top box, Side Guides, Bottom bar, Fabric, Barrel, PCB, 12 Volt Battery, Pull back Switch, Key Switch and GFS motor.
The automatic smoke or fire curtain control panel requires an Uninterruptible Power Supply (UPS) of 200 V - 200 V AC with 3 core x 1.5mm thick wire in order to keep the batteries charged up. The only function of the mains supply is to keep the batteries charged up. The power required for driving the system is taken from the included batteries. The control panel should have an Uninterruptible mains power supply under normal conditions, to ensure the proper functioning of the system. These battery shall be compatable to provide the signal for BMS monitoring.
1 | 2.8Meter height
B1-1st | 4900mm Length | Nos | 1 | 222500 | 222500
| 2100mm Length | Nos | 1 | 160000 | 160000
| 2200mm Length | Nos | 1 | 160000 | 160000
| 11250mm Length | Nos | 1 | 520000 | 520000
B1-2nd | 2100mm Length | Nos | 1 | 160000 | 160000
| 8950mm Length | Nos | 1 | 445000 | 445000
| 7830mm Length | Nos | 1 | 407500 | 407500
B1 -3rd | 4900mm Length | Nos | 1 | 222500 | 222500
| 2100mm Length | Nos | 1 | 160000 | 160000
| 8950mm Length | Nos | 1 | 445000 | 445000
B1- 4th | 4900mm Length | Nos | 1 | 222500 | 222500
| 2100mm Length | Nos | 1 | 160000 | 160000
B2 - 1F | 14700mm Length | Nos | 1 | 723750 | 723750
B2 - 2F | 2100mm Length | Nos | 1 | 160000 | 160000
B3 - 1F | 3600mm Length | Nos | 1 | 185000 | 185000
| 11200mm Length | Nos | 1 | 520000 | 520000
| 2200mm Length | Nos | 1 | 160000 | 160000
B3 - 2F | 3600mm Length | Nos | 1 | 185000 | 185000
| 9250mm Length | Nos | 1 | 407500 | 407500
2 | 6 Meter Height
B1 - GF | 3300mm Length | Nos | 1 | 328750 | 328750
| 4200mm Length | Nos | 1 | 400625 | 400625
| 5600mm Length | Nos | 1 | 522500 | 522500
| 2000mm Length | Nos | 1 | 238125 | 238125
| 6800mm Length | Nos | 1 | 770000 | 770000
| 11700mm Length | Nos | 1 | 1201875 | 1201875
| 7400mm Length | Nos | 1 | 770000 | 770000
| 6500mm Length | Nos | 1 | 657500 | 657500
| 4000mm Length | Nos | 2 | 400625 | 801250
B2 - GF | 1800mm Length | Nos | 1 | 197500 | 197500
| 10000mm Length | Nos | 1 | 882500 | 882500
| 5500mm Length | Nos | 2 | 522500 | 1045000
| 10000mm Length | Nos | 1 | 882500 | 882500
| 4700mm Length | Nos | 1 | 441250 | 441250
| 5600mm Length | Nos | 1 | 522500 | 522500
B3 - GF | 10000mm Length | Nos | 2 | 882500 | 1765000
SUB TOTAL |  |  |  |  | 17053125
GST 18% |  |  |  |  | 3069562.5
FINAL AMOUNT |  |  |  |  | 20122687.5
Terms & Conditions:
1.Payment Term: 50 % Advance againest PO and 50% before material dispatching
2. Delivery within 4-5weeks from date of release of purchase order approved drawing and advance payment.
3.Scaffolding support to hang the curtain will be provided by the client
4.However any civil work/civil modification location to install the curtain to be done by client
5.Installation is also included in the above price
6.Power supply for installation to be provided by client
7. All goods will remain the property of WindowTechs until paid for in full. We reserve the right to remove any units fitted by ourselves or others until full payment is received.
8.This quote is valid for 60 days only
9. As per Section 16 of the MSME Act, the buyer is liable to pay interest with the monthly rests to the supplier in case of non-payment or delayed payment. The interest is compounded at the rate of 24%.
Regards,
For Window Techs India Pvt.Ltd
Alistair Paiva