## Sheet1
Item Code | Item Description |  |  | Unit | Quantity | Rate | Amount
| Main Category | Sub Category | Item Detailed Specifications
27.04 |  | Curtains | Providing and fixing plastic curtains of approved shade and colour. Cost also to include the fixing of 20 mm. dia. Heavy gauge Powder coated Aluminium pipe with end brackets to hang the curtain. All complete as per instruction of designer & Architect. | Smt | 155.00
27.05 |  | Fire Curtains | "Fire Curtains" with galvanized MS head box, size( 200X200mm/ 450X200MM) powder coated, side guides size( 53x100mm) along with adjustment channels & bottom bars with motors for power up operation with standard battery backup & operated system safe fixed into steel rollers with woven glass fibre fabric, reinforced with stainless steel wire having micronized aluminium polymer coating on each side of the fabric (silver/grey) with the necessary control panel & all installation assemblies & accessories required to complete the installation. The operation shall be suitable for dedicated 240 Volts UPS, 50 Hz AC supply. Complete system shall be tested in accordance with EN 1634-1 (for 120 minutes Integrity & tested at 1000°C) BS 476-22.8 and BS 7346-3. Quoted rate shall include necessary "Emergency Retract Switch" on both sides of the curtain along with necessary control panel housed within the provided false ceiling depth with suitable supports. | Smt | 20 | 16500 | 330000
SUB TOTAL | [6 empty] | 330000
GST 18% | [6 empty] | 59400
FINAL AMOUNT | [6 empty] | 389400