## Sheet1
CLIENT : | APPLIED MATERIALS INDIA
PROJECT : | INTERIOR FIT-OUT WORKS
LOCATION : | INTERNATIONAL TECHNOLOGY PARK, INNOVATOR 1 ST FLOOR, WHITEFEILD ROAD, BANGALORE- 560066
TITLE: | BOQ FOR FIRE CURTAIN
BOQ FOR FIRE CURTAIN
SL.NO | DESCRIPTION | UNIT | QUANTITY | RATE | TOTAL AMOUNT | REMARKS
1 | FIRE CURTAIN- 2 HOURS | Nos | 1 | 140000 | 140000
Supply and installation of Fire Curtains" with galvanized MS head box, size( 200X200mm) powder coated,side guides size( 53x100mm) along with adjustment channels & bottom bars withmotors for power up operation with standard battery backup & operated systemsafe fixed into steel rollers with woven glass fibre (valmiera FGlass-UK) fabric, reinforced with stainless steel wire having micronized aluminium polymer coating on each side of the fabric (silver/grey) with the necessary control panel & all installation assemblies & accessories required to complete the installation.The operation shall be suitable for dedicated 240 Volts UPS, 50 Hz AC supply. Complete system shall be tested in accordance with EN 1634-1 (for 120 minutes Integrity & tested at 1000°C) BS 476-22.8 and BS 7346-3. Quoted rate shall include necessary "Emergency Retract Switch" on both sides of the curtain along with necessary control panel (FC01) housed within the provided false ceiling depth with suitable supports.Vendor/Manufacturer to submit valid Test Report for the complete systems and not just for fabric from an independent international accredited laboratory. The Test Report of complete system should not be more than 5 years old. Vendor/Supplier should duly submit current dated authorization letter from the manufacturer or principal that he is representing.
List of component of Fire Curtains: Top box, Side Guides, Curtains, barrel including motor, dummy end and bottom rail, Control Panel (FC01), Key switch,Override switch,etc.
Automatic Straight Fire Curtains size
Size: 1700mm (L) x 2400mm (H)
|  |  | TOTAL AMOUNT |  | 140000
|  |  | GST 18% |  | 25200
|  |  | FINAL AMOUNT |  | 165200
GENERAL NOTES
1 | No allowances shall be made to undertake rectification works if the same are so desired to be undertaken with proper adherence to recommended application procedures / standards and with approval of PM.
2 | All tracks/ fabric shall be free from scratches/stains/etc. prior to final hand over of the activity at the desired locations.
3 | Item rate to be inclusive of Packing, Forwarding, Transportation, Insurance, Loading, unloading, assembly and installation at site.
4 | Actual site measurements to be taken before production and highlighted incase of any discrepancies.
5 | Please note that the security of the material delivered on site & housekeeping of supplied product till handover is also your responsibility.
6 | All material utilised shall be as per tender recommendations and shall be fixed according to manufacturer's specifications.
7 | Finishes to be approved by the architect and there should not be any change in the quoted rates and deviations to be highlighted while quoting.
8 | Vendor to crosscheck and confirm the type and specifications of the product that they have quoted for, Any deviation from the specification above to be highlighted while quoting.
9 | Any material found to be defective shall be replaced by vendor free of cost.
10 | Vendor shall rectify all snags before handing over.
11 | Cost of disposing off packing material will be in your scope.
12 | Vendor to produce test certificate for the system.